## Slide 1: Basic Acquisition and Analysis for Machine Condition Monitoring Sam Shearman >Signal Processing & Analysis Product Manager Preston Johnson >Business Development Manager Thierry Debelle >Senior Engineer, Sound & Vibration Applications
Notes: Machine condition monitoring (MCM) is a vital component of preventative and predictive maintenance programs that seek to reduce cost and avoid unplanned downtime. MCM setups include measurement hardware and software that acquire and interpret signals generated by the machine being monitored. The presentation will discuss some of the acquisition and analysis techniques that you can apply to ensure that your MCM setup gives you reliable and cost-effective results.

## Slide 2: Your Presenters
Sam Shearman
Preston Johnson
Thierry Debelle

## Slide 3: Agenda
Machine Condition Monitoring (MCM) Defined
Elements of an effective MCM System
  Components of the Machine Measuring System
Signals and Vibration
  Information appropriate to MCM
  Dynamic signal acquisition
Getting results –Processing and Analyzing acquired data
  Level
  Trending and Alarming
  FFT Power Spectrum
  Octave
  Order

## Slide 4: Machine Condition Monitoring Defined
Tool for Maintenance and Process Control related to Industrial Machinery
  Assists with Repair / Rebuild Decisions
  Assists with Process Control and Optimization
Equipment class: Continuous or Periodic
  Continuous  Connected to Machine
  Periodic  Often Portable
Notes: Machine Condition Monitoring (MCM) systems that we’ll discuss in this presentation refer to computer-based tools for maintenance and process control related to industrial machinery. Such setups can assist with:
Repair / Rebuild Decisions
Process Control and Optimization
One way of classifying MCM systems is as either continuous or periodic, based on when and how monitoring is performed. Continuous monitoring systems are commonly attached to the machine of interest. Periodic monitoring systems are often portable and are used on multiple machines. Although we’ll focus on continuous monitoring in this presentation, much of the information will also apply to periodic monitoring.

## Slide 5: MCM System Elements
Machine
Transducers
Acquisition HW
PCI/PXI/CompactPCI PC
Measurement & Automation SW
Notes: A good place to start is with an overview of the components of a modern MCM system. These include:
The first component is the machine that you intend to monitor.
Transducers such as accelerometers, proximity probes, and thermocouples convert machine-generated signals such as sound, vibration, temperature, pressure, power consumption and others into a measurable voltage.
Cabling and perhaps signal conditioning hardware connect your transducers to a measurement instrument.
The measurement instrument here is a standard PC. As we’ll see, this offers a number of benefits. For now though, lets focus on the overall system.
Installed hardware and software converts the PC into a measurement instrument.
Acquisition hardware in the form of plug-in PCI or CompactPCI/PXI card or cards can provide signal conditioning and converts the sensor output to a computer-friendly form.
Software for measurement and automation controls our acquisition hardware, provides a monitor-site man/machine interface (MMI), and interprets acquired signals for monitoring and to assist diagnosis. It can also provide functions such as signal interpretation, report generation, and data sharing.

## Slide 6
Notes: In planning a custom machine condition monitoring system, it’s useful to consider some of the potential sources of information that your setup could monitor.
MCM-related information can be either:
Fixed / known (machine design, machine health history)
Vary with time (operating environment, operating conditions, operating parameters, machine health
The acquisition portion of your MCM system will focus on the varying information. Measurables: temperature, pressure, vibration, power, flow, and many others. Acquiring signals such as temperature, pressure, vibration, power, flow, and perhaps others is only the first step; effective monitoring systems rely on an association of available information with the machine characteristics of interest. The analysis portion of your MCM system will process measured data and analyze it in conjunction with other known information such as machine design and machine health history.
For information to be useful for monitoring, you must be able to relate it to an excitation source on your machine. It’s the job of measurement-oriented analysis to relate measurements to excitation sources due to machine operation. Doing so is important because:
Measurable responses are indirect indicators of machine response to excitation
Excitation is a function of the machine’s operating environment and operating parameters
A machine’s response to excitation is a function of machine design, operating conditions (how the machine response to excitation changes as a function of it’s operating state / environment), and machine health
Because it contains a lot of information that relates to various excitation sources, vibration is often the signal of choice for monitoring. With proper acquisition, processing, and analysis, you can relate components of your vibration signal to the components of the machine of interest.

## Slide 7: Vibration Excitation Sources
Notes: Let’s consider some vibration sources of a generic operating machine. Some vibration sources are due to machine design: slot frequency / EM related, Gears, Coupling, mechanical resonance, and bearings are some examples. Other sources result from potential problems: mechanical looseness, unbalance, and alignment. All of these vibration sources combine into a vibration signal that you can measure.

## Slide 8: The Dynamics of Vibration
Measurement viewpoints
  Static
    Level
    Trending
    Alarming
  Dynamic
    FFT
    Octave Analysis
    Order Analysis
Notes: There are several approaches to measuring vibration. One common way is to measure the overall vibration level. When you do so, you combine the signal sources together into a single aggregate measurement. As a simple example, you might check the static vibration level against some pre-defined limit to determine if manufacturer’s specifications are exceeded and maintenance is required.
Although the static measurement approach is appropriate for some applications, others require the more robust viewpoint offered by dynamic measurement. Such a measurement allows you to examine a signal in terms of the components mentioned above. As we’ll see, the dynamic vibration signal contains frequency-domain information that can be used to reduce false alarms, assess problem severity, and assist with diagnosis.

## Slide 9: Accelerometer Location
Signal Sources:
  Accelerometer on bearing mount
  Accelerometer monitoring cooling fan
Notes: What we’d like to do now is to explain some of the benefits of monitoring a dynamic vibration signal, while at the same time present some details regarding the hardware and software that goes into a machine condition monitoring system. To accomplish both of these goals, let’s consider what it takes to acquire and analyze a dynamic vibration signal.
We’re looking at a plot of a portion of a pre-acquired vibration signal generated by a Machinery Fault Simulator (MFS), which is a product of SpectraQuest, a VA based firm. Think of this setup as a generic signal source—the signals we can acquire from this device are representative of many vibration signals.
The samples in our demo show the acceleration picked up by an accelerometer attached to a bearing mount on our MFS and also as generated by a small cooling fan.

## Slide 10: Vibration Acquisition
Other common transducers for MCM with dynamic signals
  Velocity probes
  Displacement probes
  Tachometer
Accelerometer benefits
  Wide Dynamic Range
  Can convert to velocity and displacement
  Rugged, cost is coming down
Notes: Accelerometers join velocity probes, displacement probes, and tachometers as common transducers that are useful for dynamic signal acquisition for machine condition monitoring.
Accelerometers prove useful for a number of reasons. They are rugged, have a wide frequency range, and often include built-in signal conditioning. Further, you can process the acceleration signal that they pick up to convert it to displacement or velocity. On the downside, they can have poor low-frequency response, limited operating temperature range, and are sensitive to mounting techniques.

## Slide 11: Dynamic Signal Acquisition Hardware Considerations
Dynamic range (bits) 120 dB (24 bits)
Channel count 4 -16 common
Input Ranges +/-10V (variety)
Simultaneous sampling Phase / timing
Aliasing protection
Bandwidth (sampling rate) 10 kHz BW common
Signal conditioning / excitation ICPTM / Voltage Mode
Notes: Accelerometers and other transducers convert vibration into a voltage. Modern MCM systems digitize this voltage for transfer to a computer for analysis. This brings us to the next element of a machine monitoring system that works with dynamic vibration.
As mentioned earlier, this acquisition hardware might be a plug-in instrument that resides in an industrial (PXI/CompactPCI) or desktop PC. National Instruments offers a number of options for hardware that performs this function. We’ll get to these in a moment. For now, let’s consider some common requirements.
Dynamic range characterizes how well you can distinguish a low amplitude signal in the presence of high amplitude signals. A high dynamic range ensures that you won’t miss low amplitude components that are sometimes key to a successful analysis. The latest dynamic signal acquisition board from National Instruments offers 120 dB spurious free dynamic range.
Anti-aliasing filters are also required to avoid aliasing that could potentially ruin your measurement. Anti-aliasing filters are low pass variety, meaning that they will also reduce errors due to the resonance frequency of the accelerometer, as discussed earlier
The sampling frequency is usually driven by the maximum rotational speed of the machine and the highest order of interest. As a rule of thumb, min sampling rate = 5 * max rot speed * max order of interest.
Simultaneous sampling ensures that you are gathering useful cross-channel phase information
Multiple input gains allow the user to take advantage of the full dynamic range of the analyzer, on a per-channel basis
Finally, built-in signal conditioning for accelerometers and microphones (often a polarization voltage) is a nice feature, especially where space is a concern

## Slide 12: Machine Condition Analysis
Acquire and now…
  Process & Analyze
  Assess Machine Condition
  Assist with Diagnosis
For Machine Condition Analysis
  Processing = Translation
  Analysis = Comparison
Notes: After acquisition, you’ll next want to process and analyze the acquired signal to assess machine condition.
Processing for machine condition monitoring is a type of translation. Processing transforms the raw signal viewpoint from your transducer into a viewpoint that eases analysis.
Analysis for MCM often boils down to comparison: current measurements are compared to or assessed in terms of past measurements.

## Slide 13: Signal Processing = Translation
Power Spectrum Overcomes Time Domain Signal Complexity
Time Domain
Power Spectrum
Blade Pass
Motor EM Force
Rotation
Notes: So, what exactly do we mean by processing?
To answer this question, let’s continue with the acceleration signal that we showed earlier.
[[ bring up LabVIEW example, show acquired vibration signal ]]
This plot shows how the acceleration amplitude varies as a function of time. Although some repeating components are visible, the pattern appears complex. Such complexity is typical of the sound or vibration that you might measure from any operating machine.
To tame this complexity, you might apply a power spectrum, as shown here.
[[ Switch to power spectrum plot on example ]]
By depicting signal magnitude as a function of frequency, this type of analysis can often better distinguish source-related signal components. Periodic signal components appear as spikes in this graph.

## Slide 14: Demo Recap: Vibration Viewpoints
Common Vibration Viewpoints
  Time Domain
  Frequency Domain
  Orbital Domain
  Order Domain
Notes: For vibration and other dynamic signals, this part of the job is typically associated with analysis tools such as the FFT-based power spectrum, trending, and orbit plots. These tools assist by converting the signal into a form that facilitates comparison or assessment.
One way of categorizing analysis for vibration is by the domain in which the analysis is performed:
Time Domain – examines the level or shape of the vibration signal as a function of time
Frequency Domain – examines the harmonic content (repeating elements) of a signal, as a function of time frequency. The units on the X axis of a frequency domain plot are often either Hertz [Hz] or cycles-per-minute (CPM).
Orbital Domain – examines the timing relationship between two channels
Order Domain – examines the harmonic content of a signal, as a function of rotational frequency (running speed). Especially useful for varying-speed machines, because the location of orders remains fixed, even during speed variations.
These types of analysis can also be applied to other dynamic signals such as sound or power.

## Slide 15: Example Extraction – Orbit Plot
Extract the first order movements of the shaft from orthogonal positions
Use the two time domain extractions to create an XY Plot

## Slide 16: Comparison in the Frequency Domain
Fractional Octave Analysis
  Examines signals in the frequency domain
  Divides frequency domain into manageable octave bands
  Log frequency scale
Notes: To get a feel for how comparison is done with the assistance of an analysis tool, consider doing the job with fractional octave analysis. Fractional octave analysis is a type of frequency-domain analysis—it examines the frequency content of a signal. It does so by dividing the spectrum up into constant-bandwidth octave bands, which are commonly presented on a logarithmic frequency scale as a bar graph.
Fractional octave analysis proves useful for comparison of the frequency content of a signal for several reasons:
“Smart Data Reduction” – while standard FFT-based power spectrum might return 256, 512, etc, measurements, as frequency bins, Octave analysis typically returns 20 or so measurements as octave bands. Fewer measurements means that the job of comparison is simplified and that the data logging / trending portion of an MCM won’t need to churn through as much data.
Based on IEC / ANSI standards – Standards have defined how to perform fractional octave analysis, so if you work with a standards-compliant fractional octave tool (such as what’s included with the Sound & Vibration Toolset for LabVIEW), you will get consistent results that you might compare with other measurements taken under the auspices of the same standard.

## Slide 17: Fractional Octave Signature Analysis
Fractional-octave-based comparison
Confidence intervals define pass/fail bands
Set of pass/fail bands  Signature / Baseline
Notes: [[ Run Fractional Octave Limit Mask Testing Demo here ]]
The demo uses the Fractional Octave Analysis feature of the Sound & Vibration Toolset for LabVIEW. It defines a signature, which is a basis for comparison, by calculating a set of confidence intervals based on a confidence level that you specify. The confidence intervals are defined based on variations seen in the octave bands during a block-based octave analysis. This baseline provides a reference for later comparison with signals from the working machine. More specifically, it defines limits in which the signal can reside and not flag a fault or warning.

## Slide 18: Demo Questions, Answers, and Possibilities
What’s the benefit?
Notes: Preston: So, what’s the benefit of applying this type of signal processing and analysis to machine condition monitoring?
Sam: One big benefit is best seen when you compare what this is doing to the limit testing or trending that you might perform with a static measurement of vibration. With that type of measurement, you are comparing an overall signal level, which encompasses all frequencies to a set of limits. With fractional octave analysis, your comparison is a function of signal frequency content and you can program your monitoring system to ignore frequency bands associated with noise or pay extra attention to frequency bands associated with vital machine components.
As an example, if you are monitoring a machine that’s located near a loading bay, you might have the MCM system ignore frequency bands that you know are associated with the sound and vibration associated with trucks or loading. At the same time, you could have your system to flag warnings when frequency bands associated with bearing frequencies change. By ignoring noise, and watching only signals of interest, your MCM system will be less prone to false positive warnings!

## Slide 19: Analysis and Beyond
After Acquisition, Signal Processing, and Analysis
  Report Generation (HTML)
  Data Sharing (between programs or across the network)
  Remote Monitoring (Across Inter- or Intra-net)
  Much more…
Notes: What we’ve demonstrated thus far involved acquisition, signal processing, and analysis that you can apply to machine condition monitoring. These elements might serve as a portion of a front-end for a comprehensive machine condition monitoring system. By sharing data over a LAN or even the Internet, you could, for instance, monitor multiple machines, generate HTML status reports, and remotely check in on plant status from a home PC.

## Slide 20: MCM with National Instruments HW & SW
Performance
Cost
Integration
Rapid Development
Notes: The setup we’ve described and demonstrated is just one possible approach to machine condition monitoring. When you work with the National Instruments hardware and software platform, you are free to build a completely custom machine condition monitoring system that fits exactly your machine condition monitoring needs.
National Instruments offers PC-based hardware and software tools with which you can build custom machine condition monitoring system. This PC-based approach has a number of benefits:
Lower cost through inherent economy of scale
Open platform is flexible and multi-vendor
Use of continuously improving technology means future updates can apply latest high-speed computing technology
Development tools designed specifically for measurement and automation applications such as machine condition monitoring

## Slide 21: Vibration Monitoring System Diagram
Machine
Transducers
Acquisition HW
PCI/PXI/CompactPCI PC
Measurement & Automation SW
Notes: Let’s discuss some of the hardware and software that we used to acquire and analyze the signals we’ve been showing you.

## Slide 22: Acquisition Hardware
NI 4472 for PXI
8 simultaneously sampled inputs
120-dB dynamic range
104.2 kS/s, 47-kHz bandwidth
Multi-board synchronization, up to 56 or 112 channels in one PXI chassis!!!
ICPTM signal conditioning

## Slide 23: Other Possible Signal Sources
Integrate signals & functionality “As Needed”
  Temperature
  Pressure
  Flow
  Level
  Images – Light or Thermal!
Notes: Although our presentation and demos have involved dynamic vibration measurement, there are a number of other available signals to consider when building a machine condition monitoring system. We’ve already mentioned measurement of static vibration signals, other common possibilities include temperature, pressure, flow, and level. National Instruments offers plug-in PC-based hardware for these signal types as well as signal types and functionality for cutting edge machine condition monitoring. For instance, you can use a National Instruments IMAQ image acquisition card to acquire thermographic images from an infrared camera to show casing temperature.

## Slide 24: Machine Condition Monitoring with LabVIEW 6i
Rapid application development for measurement and automation
Industry Standard
Built-in tools for Measurement Analysis
  Level, FFT-Power Spectrum, Cross Power Spectrum, Limit Mask Testing
Internet
  Publish or Receive Data with Datasocket
HTML Report-Generation Tools
Many Add-ons and support resources
Notes: As mentioned earlier, software running on your PC provides a man/machine interface, controls your instrumentation, performs signal processing and analysis, handles report generation, and shares data over the Internet. National Instruments LabVIEW 6i is a graphical application development tool that allows you to rapidly build applications with these and other functions. The only true graphical programming language, LabVIEW strikes an ideal balance between ease of use and unlimited functionality.
LabVIEW includes many analysis routines that you can apply for MCM. Among the included tools are a set of Measurement Analysis VIs that that input raw data and output measurements. What this means is that results are appropriately scaled, with engineering units and are ready to graph or display. You can easily deploy these routines in your own code to implement such measurements as:
DC/RMS (Level), Power Spectrum, Cross Spectrum, Frequency Response, Extract Single Tone (Tone Detection), Software Triggering, Peak Detection, Digital Filtering, Signal Generation, and Limit Mask Testing
Other features of LabVIEW allow you to easily publish and receive data over a network and generate reports. Controls and indicators in LabVIEW 6i all support Datasocket, a protocol that allows program-to-program communication and data transfer on the same computer (between applications) or across a network. LabVIEW 6i also includes tools that allow you to easily create HTML-based reports. The results are ready to display with browsers such as Netscape Navigator and Microsoft Explorer.

## Slide 25: National Instruments Software for Sound & Vibration Analysis
Toolsets extend LabVIEW:
  Sound & Vibration Toolset – ANSI / IEC compliant Fractional Octave Analysis, Level Measurements, Calibration, Weighting Filters
  Order Analysis Toolset – tools related to analysis of dynamic signals generated by rotating or reciprocating machinery
Notes: LabVIEW ships with tools for signal processing analysis that are general purpose, meaning that they can be applied for machine condition monitoring as well as many other engineering jobs. For specific functionality, we offer a number of add-on toolsets, several of which are applicable to machine condition monitoring.
The Sound and Vibration Toolset offers functions and visualization tools for fractional-octave analysis, sound level measurements, frequency analysis, transient analysis and calibration.
The Order Analysis Toolset gives you tools for processing and analysis of harmonic orders, signal components (from vibration, sound and other dynamic signals) that are related to the running speed of your machine.

## Slide 26: Summary
Elements of an effective Machine Condition Monitoring System
  Understanding the Problem
Acquisition of Dynamic Vibration
  Information appropriate to MCM
  Appropriate acquisition
Analysis as Comparison
  Analysis Tools assist comparison
Notes: The National Instruments tools-based approach applies to end-users with machinery they would like to monitor. End users can develop their systems internally with our platform or they can work with a maintenance consultant to get the job done. Our platform is also valuable for maintenance consultants looking for a consistent off-the-shelf platform with which to develop for their customers.
Please contact us to discuss your specific requirements!

## Slide 27: Thank You for Attending!
http://www.ni.com/info with info code 2001MCM
Preston Johnson
  Business Development Manager
  (512) 683-5444
  preston.johnson@ni.com
Sam Shearman
  Product Manager, Signal Processing and Analysis
  sam.shearman@ni.com
Notes: Please contact us to discuss your specific requirements!