## Slide 1: Wireless Communications for Data Acquisition and I/O
David Potter
Wed Aug 16
10:15-11:30 a.m., 1:45-3:00 p.m.
Hickory (9C)

## Slide 2: Outline
Why wireless?
Overview of wireless technology
  Narrowband Radios
  Spread Spectrum
Wireless spectra and standards
  ISM bands
  Wireless LANs
  Wireless WANs
Wireless measurement and automation systems
  FieldPoint™ with FHSS modem (900 MHz)
  High-Speed DAQ using IEEE 802.11 (ViaSAT)
Applications and case studies

## Slide 3: Why Wireless?
Wires are expensive to install and maintain
  Typical chemical plant – $40/ft
  Nuclear power plant – $2000/ft
Wiring is sometimes difficult or impossible
  Moving/turning platforms
Distance
Temporary or mobile applications
Convenience
Notes: The general reason to use wireless, of course, is to avoid or minimize the use of wires and cables. Depending on the nature of the application and environment, physical wiring can be expensive, inconvenient, or even impossible. Examples include moving/turning platforms, mobile applications (vehicles, cranes, and so on), and structures that complicate installation of wiring. More traditional applications that perhaps are not permanently operated benefit from wireless because you do not need to install, remove, and reinstall wiring and cabling.
Wireless communications also extends the distance, or range, of data acquisition and I/O beyond what is practical with wiring. Therefore, large scale operations, such as water treatment facilities and tank farms, widely use wireless technologies.

## Slide 4: Wireless Technologies – Two Types
Narrow band radios
  High-power, good signal bounce
    Long distance
  Requires FCC license to operate
  Limited bandwidth (9600 bps typical)
Spread spectrum
  Limited to 1 W power (0.1 W in Europe)
  Line of sight required for long ranges
  Immune to interference
  High bandwidth
  No FCC license required
Frequency
Power Spectral Density
Narrowband
Spread Spectrum
Noise Level
Notes: Traditionally, users performed telemetry and remote monitoring using narrowband radio modems. These packet radios operated in the VHF and UHF bands bands (i.e., 150 MHz, 450 MHz, 928 MHz) at high output powers. Operation of these narrowband radios requires a site license from the Federal Communications Commission (FCC). Because the bandwidth is limited to 25 kHz, data rates are also low, typically 960-000 bits/s. However, the high power capabilities of narrowband radios make them popular for applications that require long distances or communication through obstructions (such as trees, walls, and so on).
One example of a narrowband radio modem is the TS4000 from Teledesign Systems (teledesignsystems.com/ts4000.html). The TS4000, which has been used in applications with Serial (RS-232) FieldPoint, operates at UHF and VHF frequencies, and can operate at an output power of up to 5 W (and up to 100 W with external amplifiers). Teledesign radios are distributed by National Instruments Alliance member Sage Designs, Inc. (sagedesignsinc.com).
Spread spectrum devices spread the information across a wide bandwidth, reducing the signal power density so that it does not create interference. The spreading of the frequencies makes the system immune to interference and noise. In addition, the wider bandwidth translates to higher data rates. However, because spread spectrum systems are limited to 1 W output power (0.1 W in Europe), distances heavily depend on line-of-sight availability. However, spread spectrum devices operated at specified frequencies are license-free, requiring no license or permit to use.

## Slide 5: Spread Spectrum - History
First developed and used in World War II
First patent on spread spectrum
  Hedy Lamarr and George Antheil
  Idea to unjam radio-controlled torpedoes
  Suggested using player piano rolls to synchronize transmitter and receiver
Notes: Spread spectrum dates back to World War II, when both the Allies and Axis experimented with spread spectrum techniques for secure radio transmissions, particularly as countermeasures for navigation beacons, communications, radar, and missile control. Interestingly, the first patent for “Secret Communications System” in 1942 belongs to actress Hedy Lamarr and musician George Antheil. Lamarr, who was somewhat of a technologist at the time, became interested in ways to unjam a radio-controlled torpedo. Inspired while sitting at a piano with Antheil, Lamarr conceived the idea of moving the radio signal from frequency to frequency at split-second intervals. Antheil, who worked extensively with player pianos, suggested using player piano rolls to synchronize the frequency pattern in the transmitter(controller) and receiver (torpedo).

## Slide 6: Spread Spectrum History – Cont.
In 1980, FCC allocates three bands for license-free spread spectrum devices
  915 MHz, 2.4 GHz, and 5.8 GHz
  1 W limit on power output
Spread spectrum migrated into several commercial applications
  Cell phones, PCS, GPS, WLAN, Bluetooth
Notes: In 1980, the FCC allocated three industrial, scientific, and medical (ISM) bands for secondary usage by spread spectrum devices (Part 15). Part 15 authorizes the unlicensed operation of spread spectrum transmitters within the 915 MHz, 2450 MHz, and 5800 MHz frequency bands at higher power levels (up to 1 W) than would normally be permitted for other unlicensed devices. When operating at 1 W output power, the maximum directional gain of the associated antenna may not exceed 6 dBi, resulting in a maximum isotropically radiated power (EIRP) of 6 dBW.
In the last several years, we have seen rapid adoption of spread spectrum technology into commercial applications, such as digital cellular telephone, PCS, GPS, wireless LANS such as IEEE 802.11, and Bluetooth.

## Slide 7: Two Types of Spread Spectrum
Frequency hopping spread spectrum (FHSS)
  Carrier frequency changes (hops) many times per second
  Pseudo-random pattern
Direct sequence spread spectrum (DSS)
  Carrier is modulated with pseudo-random code (at higher frequency)
Time
A
B
C
D
E
F
G
H
I
J
Frequency
dBm
Frequency hopping
Direct Sequence
Bit stream (data)
Chip stream
Pseudo-random code generator (chips)
Notes: There are two common approaches to implementing spread spectrum communications –frequency hopping and direct sequence.
Frequency hopping systems convert data into packets, transmitting individual packets at separate frequencies in a rapid, pseudo-random hopping pattern that uses at least 50 channels. If a packet is not received correctly, because of interference for example, the packet automatically retransmits at a different frequency. The receiver is synchronized with the transmitter to decode the frequency hopping signal.
Direct sequence spread spectrum systems encode the data to transmits with a higher-frequency pseudo-random data stream (also called chips), transmitting the result in a broadband signal equally spread across the available bandwidth. The receiver uses the same pseudo-random data stream to decode the data.
Both types of spread spectrum systems have advantages. Direct sequence does not incur hopping overhead and may therefore yield higher data rates. The main strengths of frequency hoppers are reliability and interference immunity. When a frequency hopper encounters strong interference at a particular channel, data is automatically resent at a different channel. This makes frequency hoppers immune to problems caused by noise, jamming, other transmitter devices, and multipath fading. The inherent data reliability of frequency hopping makes this technique ideal for industrial environments.

## Slide 8: Spread Spectrum Technologies
Notes: This display compares the frequency spectra of frequency hopping and direct sequence signals.

## Slide 9: Effect of Interference
Frequency hopping
  Interference causes retransmits at different frequencies
Direct sequence
  Low narrowband noise has no effect
  At some interference level, signal fails (not gradual)
Throughput
Interference level
FHSS
0%
100%
Throughput
Interference level
DSSS
0%
100%
Notes: FHSS and DSSS both have advantages and disadvantages. Overall, performance is determined more by the quality of the implementation and radio and less on the core spread spectrum technology.
One difference in FHSS and DSSS is performance in the presence of noise and interference. With FHSS, a signal that is interfered or corrupted at one of the frequency hops is automatically retransmitted at a different frequency. Although no information is lost, this slows down throughput. Therefore, performance degrades in a linear fashion with increase in noise/interference.
With DSSS, however, low levels of narrowband noise have no effect on performance, as the coded signal is equally spread across a wide spectrum. With increasing noise power, however, there is a point at which the DSSS radio fails. If the DSSS radio supports a second channel, then the radio can automatically try retransmitting on a second channel; otherwise the communications cease. Therefore, throughput as a function of noise level is represented as a step function.

## Slide 10: Outline
Why wireless?
Overview of wireless technology
  Narrowband radios
  Spread spectrum
Wireless spectra and standards
  ISM bands
  Wireless LANs
  Wireless WANs
Wireless measurement and automation systems
  FieldPoint™ with FHSS modem (900 MHz)
  High-Speed DAQ using IEEE 802.11 (ViaSAT)
Applications and real world issues
Notes: The following section briefly surveys the prevalent wireless standards, including ISM bands for license-free spread spectrum, wireless LAN standards, and wide area network (WAN) wireless standards.

## Slide 11: ISM Bands
In 1980, FCC allocates three bands for devices to operate as secondary devices (Part 15)
  902 – 928 MHz (28 MHz)
  2.4 – 2.483 GHz (83.5 MHz)
  5.725 – 5.85 GHz (125 MHz)
  1 W limit on power output
Notes: In the United States, the FCC governs all radio transmissions, including those employed in wireless LANs. Other nations have corresponding regulatory agencies, such as CEPT in Europe
As mentioned earlier, the FCC designated three instrumentation, scientific, and medical (ISM) bands for license-free usage by a ‘secondary’ device. These ‘secondary’ devices must not interfere with ‘primary’ users of the bands, and are therefore required to use either FHSS or DHSS spread spectrum techniques, with output power limited to 1 W. These include 902-928 MHz, 2.4-2.483 GHz, 5.15-5.35 GHz, and 5.725-5.875 GHz.

## Slide 12: Wireless Spectra (ISM Low Bands)
26 MHz
902 MHz
928 MHz
83.5 MHz
2.4 GHz
2.4835 GHz
125 MHz
5.725 GHz
5.85 GHz
1 W
FCC
83.5 MHz
2.4 GHz
2.4835 GHz
30 MHz
5.785 GHz
5.815 GHz
0.1 W
CEPT
26 MHz
2.471 GHz
2.497 GHz
Japan
Notes: The regulatory agency for Europe, CEPT, allocates similar bands for unlicensed usage. However, power levels for CEPT are 100 mW (instead of the 1 W allowed by the FCC). In Japan, a 2.4 GHz frequency band is available. Most countries follow one of these agencies for spectra allocation. As you can see in the graphic, the three allocations coincide at the 2.4 GHz. Individual countries typically have specific rules and regulations regarding the use of these bands.

## Slide 13: Wireless LAN Standards
IEEE 802.11
  wireless ethernet
HiperLAN
  Developed in Europe
  Type 1 – wireless LAN for computer networks
Bluetooth
  Cable replacement for computer peripherals, mobile phones, and handheld devices
HomeRF
  Home networking
Notes: In addition to IEEE 802.11 (discussed on following slide), popular wireless LANs include HiperLAN, Bluetooth, and HomeRF.
HiperLAN is a high-performance wireless LAN standard developed in Europe by the ETSI organization. HiperLAN is complementary to IEEE 802.1 and other 802 standards, and supplies higher data rates. HiperLAN Type 1 specifications include
– 5.2 GHz frequency (not spread spectrum)
– 23.5 Mbps data rate
– range of about 50 m
Bluetooth is a standard for low-cost, low-power wireless solutions targeted at short-distance connection of devices (such as computer peripherals, mobile phones, handheld devices, and PDAs). Bluetooth has a high level of industry backing, and is now becoming commercially available. Specifications include
– 2.4 GHz, FHSS
– 1 Mpbs data rate
– 10 m range (higher power devices are optional)
HomeRF is a wireless networking standard targeted at in-home networks. Key specifications include
– 2.4 GHz, FHSS
– 1 or 2 Mbps data rate
– range of about 50 m

## Slide 14: IEEE 802.11 – Wireless LAN
Wireless Ethernet
FHSS or DHSS, 2.4 GHz
Data rate – 1 or 2 Mbps today
  802.11b – 11 Mbps (becoming available)
  802.11a – 54 Mbps operating at 5.8 GHz (future)
Compatible with wired LANs
Physical layer
Data link layer
FHSS
2.4 GHz
802.11 MAC
CSMA/CA
DSSS
2.4 GHz
Infrared
IEEE 802.11
OSI model
Notes: IEEE 802.11 is a standard for wireless LANs, sometimes referred to as ‘wireless Ethernet.’ Finalized in 1977, IEEE 802.11 specifies one medium access control (MAC) protocol layer, and three physical layers (frequency hopping, direct sequence, and infrared). The FHSS and DSSS specifications operate in the 2.4 GHz band and currently deliver data rates of 1 Mbps and 2 Mbps. Faster devices operating at 11 Mbps are available, and the standards group is investigating even faster data rates. The MAC protocol layer operates using CSMA/CA, as well as a polling mode.
IEEE 802.11 delivers interoperability among devices, in much the same way that Ethernet devices are interoperable at the PHY/MAC layers. While IEEE 802.11 devices with the same physical layer implementation may be interoperable, there is some concern that the specification is not complete enough yet to ensure true interoperability.

## Slide 15: Wireless Wide Area Networks
Remote, distributed (nationwide, global)
Modems connect Serial device to wireless network
Some options
  Packet radio services
    RAM/Mobitex
    ARDIS/Modacom
  Cellular digital packet data (CDPD)
  Data over analog and digital cellular
    GSM, CDMA, and so on
  Two-way paging network
  Satellite
Notes: When you collect data from remote sites, and a wired connection is not available, there are a number of wireless services that provide wide area coverage. Briefly, some of the options include:
Two-way packet radio networks – operated by service providers that offer wireless data communications to the public, and also to services such as police, fire, and ambulance services. Examples include the RAM/Mobitex system, and the ARDIS/Modacom system.
Cellular digital packet data (CDPD) – a relatively new technology that transmits data packets over the existing analog cellular network. You can use CDPD as a wireless extension of an existing TCP/IP network. CPCDis offered by voice cellular network operators who wish to add wireless data to their existing services. CDPD modems are available with RS-232 connections.
Data over analog/digital cellular –includes the traditional analog modem approach, as well as the new digital cellular networks, such as GSM and CDMA.
Two-way paging network – the technology augments traditional paging with two-way communications, making it more appropriate for telemetry and data acquisition. The paging technology offers good coverage, but slower data throughput rates.
Satellite – when you require access to remote regions, you can use satellite networks for telemetry and data acquisition applications.

## Slide 16: Outline
Why wireless?
Overview of wireless technology
  Narrowband radios
  Spread spectrum
Wireless spectra and standards
  ISM bands
  Wireless LANs
  Wireless WANs
Wireless measurement and automation systems
  FieldPoint with FHSS modem (900 MHz)
  High-Speed DAQ using IEEE 802.11 (ViaSAT)
Applications and real world issues

## Slide 17: Wireless FieldPoint
Industrial wireless modem
  900 MHz
  Frequency hopping
Up to 20 mile range with line of sight
  Repeaters, remote antennas can help obtain line of sight
Works with Serial (RS-232) FieldPoint
Software-transparent
Notes: One of the current options for wireless I/O is wireless FieldPoint, which consists of a 900 MHz spread spectrum wireless modem (SRM6000) and Serial (RS-232) FieldPoint. The wireless modem comes pre-configured to work with the FP-1000 RS-232 module (which connects directly to the modem with a serial null modem cable included with the modem). The modems are completely software transparent.
The SRM6000 spread spectrum modems operate at the 900 MHz bandwidth using noise immune frequency-hopping technology. The modems also deliver relatively long distances, up to 20 miles with line of sight. Because they operate at 900 MHz, you can only use them in the Western Hemisphere (North, Central, and South America).
For applications outside of this region, you can use a similar approach with available wireless modems that are commercially available at the appropriate frequencies in the country of interest. For example, National Instruments identified a 2.4 GHz wireless modem (FHSS) that works with FieldPoint and has the CE and ETSI approvals for use throughout most of Europe. The digital wireless HopNet-1510 has been tested with FieldPoint, and you can find more information at digital-wireless.com/hopn.htm
Again, for licensed radio applications, the Teledesign TS4000 radio has been successfully used in applications with FieldPoint. For more information on the UHF/VHF radios, go to teledesignsystems.com/ts4000.html, or contact Sage Designs, Inc at sagedesignsinc.com

## Slide 18: Wireless FieldPoint – Topologies
Point-to-point, and point-to-multipoint
Repeaters extend range, navigate obstacles
You can reconfigure radios as masters, slaves, or repeaters
Master
Slave
Slave
Slave
Repeater
RS-485
Notes: AT1A– <number>
Wireless Communications for Data Acquisition and I/O
<header>
<date/time>
You can use the wireless FieldPoint system using the 900 MHz SRM6000 radio modems in a number of different configurations. The radios support point-to-point and point-to-multipoint systems. In a typical configuration, a master radio is connected to a PC. Each remote FieldPoint bank connects to a slave radio. Use repeater radios to extend the range, or navigate the signal around obstacles.
A unique network ID number identifies the radios to each other. For even more security, you can use a unique seven-digit ID number assigned to each radio. A transmitter or receiver must be pre-configured with valid ID numbers to communicate. In either case, multiple networks of radios can coexist because of the unique ID numbers.
Master, slave, and repeater radios are physically identical. In other words, you can reconfigure any radio to operate in any of these modes. Perform configuration using a terminal emulator program, such as HyperTerminal.

## Slide 19: MiniDAT – Wireless Networked DAQ
Standard software
  NI-DAQ remote call (RDA)
  TCP/IP protocol
IEEE 802.11 wireless LAN
  2.4 GHz, DSSS
DAQCard-1200
  Compatible with SCXI
Rugged mechanical design
  Resistant to shock, vibration, water
Notes: Another wireless data acquisition option is the ViaSat MiniDAT – a rugged, wireless DAQ device manufactured and distributed by ViaSat (viasat.com/minidat).
The MiniDAT is a compact, rugged unit that incorporates an NI DAQCard-16XE-50 multifunction I/O PC card, and a wireless LAN card. The MiniDAT uses standard networking technology, including TCP/IP and NI-DAQ remote calls (RDA). Therefore, you can use all of the standard NI-DAQ functions without modification. NI-DAQ uses RDA to transfer the function calls across the network, which in this case is an IEEE 802.11 wireless LAN connection, (2.4 GHz, DSSS) to the MiniDAT.
The MiniDAT is particularly useful when standard DAQ and SCXI function is required, including higher speed waveform I/O.

## Slide 20: ViaSat MiniDAT – Topologies
MiniDATs are IP-based network nodes
Connection to PC and/or network via
  PC card adapter
  Access point
WLAN PC card
Access point
Ethernet
MiniDAT
MiniDAT
MiniDAT
MiniDAT
Notes: AT1A– <number>
Wireless Communications for Data Acquisition and I/O
<header>
<date/time>
Because the MiniDAT is based on IEEE 802.11, topologies are similar to wired Ethernet. For simple point-to-point applications, you can use a PC card wireless adapter. Alternatively, you can use a wireless hub device, typically referred to as an access point, to connect IEEE 802.11 segments to standard Ethernet. In this configuration, any PC connected to the network that has NI-DAQ installed could access and control the MiniDAT through its IP address.

## Slide 21: Comparison
 | Wireless FieldPoint | MiniDAT
I/O capabilities | FieldPoint I/O (Serial) | DAQCard-16XE-50
Acquisition speed | <10 S/s | >100 kS/s
RF technology | Frequency hopping 900 MHz | Direct sequence 2.4 GHz
Topology | Modem with RS-232 port | IEEE 802.11 (wireless LAN)
Range | 20 miles | ~1000 ft
Operating temperature | -40 to 70 °C | -30 to 60 °C (DAQCard re-calib.) 0 to 37 °C (w/o DAQCard re-calib.)
Size | 13 x 20 x 4 cm (plus FP) | 10.6 x 20 x 3.6 cm (total)
Notes: The wireless FieldPoint and the MiniDAT offer two solutions for wireless data acquisition and I/O applications. The table above highlights the key attributes of both systems.

## Slide 22: Case Study – ViaSat MiniDAT
SCXI
MiniDAT
DAQCard
WLAN PC Card
Notes: One example of wireless DAQ and SCXI™ is from the diagnostic service group within AstenJohnson, a company that makes products and provides services for the paper industry. This group helps the customer troubleshoot, identify, and offer possible solutions to machine productivity issues.
When a problem can not be identified using conventional methods, the company uses electronic diagnostic equipment to measure process instabilities. Through the introduction of pressure sensors into stock lines, triggers on stock delivery rotating elements, in-line measurement of stock consistencies, placement of vibration sensors on machine structural elements, and electronic monitoring of machine process signals, such as basis weight and opacity, electronic data is simultaneously taken regarding machine performance.
All signals (pressure, vibration, triggers, and specialty sensors) are conditioned using National Instruments SCXI-1001, 12 slot chassis, controlled by a DAQCard-AI-16XE-50 PCMCIA card and LabVIEW software. The sensors are distributed throughout the machine, and can span distances of 400 to 500 ft., requiring stringing and routing long cables around section drives, line shafts, and stock chests.
MiniDAT provides a high-speed, multi-channel, wireless link between the process signals and laptop PC. Using the capabilities of the MiniDAT eliminates the need to run long cables from one end of the machine to the other making set up easier, faster, and safer. Each MiniDAT has its own IP address making it possible to access several devices at various locations on the machine, also supporting Internet access.

## Slide 23: Case Study – SRM6000 Modem
Camrosa Water District
  Uses more than 50 SRM6000s to communicate from municipal headquarters to remote stations
    HMI, pumps, tanks, sewer lifts
  Hilly terrain of Ventura County, CA
    Uses four repeaters
  Military based located next door (high RFI)

## Slide 24: Case Study – SRM6000 Modem
Allegheny Ludlum Steel
  Uses SRM6000s on roaming AGV system in steel plant
  One SRM6000 master covers entire plant
    Three AGVs communicate with master
    Not line-of-sight
    Lots of steel in the way
    Extreme temperatures

## Slide 25: Where to Get More Information
Wireless FieldPoint
  ni.com/fieldpoint
DataLinc modems
  data-linc.com
Teledesign licensed radios
  teledesignsystems.com/ ts4000.html
Digital wireless modems for Europe
  digital-wireless.com/hopn.htm
MiniDAT
  viasat.com/minidat
IEEE 802.11
  http://grouper.ieee.org/groups/802/11/
Spread spectrum scene
  sss-mag.com
Notes: The Web sites for the products mentioned in this session are listed above, along with a couple of sites that offer background and tutorial information, such as spread spectrum scene online, and the IEEE 802.11 site.

## Slide 26: Summary
Wireless technology evolving rapidly
Standards are developing
You can use it today
Questions?