## Slide 1: Advanced SCADA Using Lookout™
Ross Houston
Lookout R&D Manager
Wed Aug 16
12:00-1:15 p.m., 3:30-4:45 p.m.
Mulberry (10B)

## Slide 2: Outline
Lookout basics
Connectivity
Citadel database
Networking
Advanced process design

## Slide 3: Lookout Basics
Object oriented
Event driven
No programming
Notes: Lookout is object-oriented in that all functionality and data is contained in objects. Developing a Lookout application is a matter of creating, configuring, and connecting objects. Objects are software representations of everything from potentiometers and switches to PLCs and RTUs connected physically to the computers you have running Lookout.
An important concept to understand is that Lookout is entirely event-driven, not loop-driven. To understand the significance of this design requires a digression, to explain how standard loop-driven programs work.
Loop-driven applications execute code sequentially from top to bottom, and loop back to the top to execute the same code over and over. In this programming model, a given section of code or rule may execute millions of times before the result changes. This wastes computer processor time and slows down responses to frequent events. In contrast to this programming model, Lookout is entirely event-driven. Each object remains quiescent, doing nothing until an event occurs. An event is a change in a data value. When an incoming signal changes, the object activates, processing the value according to its functionality. Objects only send out signals when the result of their processing changes. This is how an event propagates throughout your system, creating a chain-reaction that affects only the objects in the chain.
This process of creating, configuring, and connecting objects does not require programming knowledge.

## Slide 4: Lookout Objects
Functionality and data contained in objects
Two different ways to connect objects
  True connections
  Remote connections
Tools to manage objects
  Object Explorer
  Connection Browser
Notes: A Lookout object is a self-contained software unit designed to do something specific in your HMI/SCADA application. What each object does is generally referred to as its functionality. Each object has a set of data members you can log to a predefined database, and a set of parameters.
There are two ways to connect objects in Lookout – true connections and remote connections. When a true connection is made between two objects, the writer is considered the owner of the value. When a remote connection is made, the object being written to is considered the owner of the value, and the writing object is subscribing to the value and requesting changes.
With Object Explorer, the user easily manages objects you’ve created. You can organize them hierarchically into folders. Many of the menu items commands that are object-specific are available here as right-click menus. Object Explorer also serves as a palette-style tool to drag and drop expressions onto panels.
With Connection Browser, the user visualizes connections between objects. You can easily follow a chain of connections to troubleshoot your logic. Many object-specific commands are also available here as right-click menus.

## Slide 5: Object Types
UI objects
  Pot
  Switch
Driver objects
  Modbus
  FieldPoint
Calculation
  Derivative
  Histogram
Control
  Flip flop
  Neutral zone
Batching
  Datatable
  Sequencer
Timers
  One shot
  Time of day
Notes: Pot is a numeric control object. You can think of it as a numeric variable.
Switch is a logical control object.
Driver objects communicate with your hardware via serial, card-based, or Ethernet communications.
Derivative dynamically calculates the derivative of a numeric input.
Histogram samples a numeric input, and provides numeric outputs that correspond to the values of a standard histogram chart.
A flip flop emulates a standard JK flip flop in software by changing the state of its logical output when its logical input pulses true.
Neutralzone is an on/off controller. It functions the way a home air conditioning thermostat does; if the temperature rises above a certain level, the above data member goes true (turning the A/C on). When it drops below a lower temperature, the below data member goes true (turning the A/C off).
A DataTable contains a matrix of rows and columns, much like a spreadsheet. A cell value is numeric, logical, or textual.
The sequencer object is a method for cycling through a collection of up to 100 differently configured on/off states for your process.
The Lookout timer objects all have single logical outputs with the pulse high or low depending, on the state of the timer.

## Slide 6: Connectivity
Lookout driver objects
OPC
DataSocket
DDE
ActiveX
Notes: Lookout driver objects come with every package of Lookout at no additional cost. They provide access to various NI hardware and third party hardware.
With OPC (OLE for Process Control), an industry standard, hardware manufacturers write drivers for their hardware (OPC servers) that can be used everywhere.
DataSocket is a NI technology that facilitates communication between NI software packages.
With DDE (Dynamic Data Exchange), a widely implemented Microsoft technology, data exchanges between applications and across a network.
With ActiveX, a Microsoft technology, software objects (ActiveX controls) are imbedded in applications that support ActiveX (ActiveX containers).

## Slide 7: Lookout Driver Objects
For NI hardware
  FieldPoint™
  DAQ™
  Fieldbus
For third party hardware
  Modbus
  Allen Bradley
  Tiway
Drivers written by third parties
Notes: The datamembers of a Lookout driver object mirror the data available on the targeted hardware. For example, the Modbus object contains a set of datamembers named 40001 - 49999 that represent those registers on the device.
Driver objects also contain input datamembers to control polling. There is a logical datamember (Poll) that tells the object to read new values from the device when the datamember pulses high. There is also a numeric datamember that tells the object to poll periodically, every X seconds. The objects also have status datamembers that give you more information about the state of the device and/or the communications link.
We, in Lookout R&D, write these driver objects for our own hardware as well as for third party hardware. NI also sells a toolkit with which users write their own drivers (or any other kind of object for that matter) in C++.

## Slide 8: OPC
NI products
  LabVIEW DSC
  FieldPoint
  DAQ
Third party servers

## Slide 9: Other Methods of Connectivity
DataSocket
  LabVIEW™, Measurement Studio™
DDE
  Excel, numerous third party applications
ActiveX
  Insert ActiveX controls into your process as Lookout objects
Notes: DataSocket implements an easy-to-use, high-performance programming tool that is designed specifically for sharing and publishing live data in measurement and automation applications. For more information about DataSocket go to ni.com/datasocket
With dynamic data exchange (DDE), a widely implemented Microsoft technology, data exchanges between applications and across a network. Lookout can act as a DDE server or a DDE client. A common usage of this capability is a live connection between Lookout and Excel. For more information about DDE go to msdn.microsoft.com/library/default.asp?ShowPane=false&URL=/library/psdk/winbase/dde_4oit.htm
With Lookout 4.5, you insert ActiveX controls into your process and use them like you would use any other Lookout object. For more information about ActiveX go to activex.org or microsoft.com/ActiveX

## Slide 10: Citadel Database
Event driven database
Log data via each object’s associated database
View Citadel data
  Hypertrend object
  Citadel ODBC driver
Notes: Lookout logs data only when the value of a point changes, not at a timed interval. The logged data accurately reflects the actual behavior of the point being logged because the same value of a point is not recorded over and over. With Citadel, disk usage is exactly proportional to the amount of information recorded.
After the data is stored to disk, you can view it with a HyperTrend object in Lookout or with SQL. HyperTrend objects serve as windows into your database. With SQL, an industry-standard language supported by most database packages, other applications directly retrieve data from Citadel.
Because Citadel uses Universal Coordinated Time (UCT) to time stamp the data, you do not need to compensate for data logged in different time zones. The HyperTrend object automatically converts from universal to local time before displaying a data history.

## Slide 11: Networking
Multiple servers and clients connect
Our own reliable IA-specific protocols implemented on top of UDP
  Real time data
  Historical data
  Alarm and event data
No additional setup is required if Microsoft TCP/IP is configured correctly on your computer
Notes: Making a connection across the network works exactly like making a connection on the same machine. All of the network communication is transparent to the user.
We implemented our own set of network protocols tailored for the kinds of data typical to an industrial automation system. On top of UDP, we implemented our own socket layer protocol. On top of this socket layer, we implemented several higher level protocols, each with a specific type of data in mind. For example, we have a protocol for real-time data, a protocol for historical data, a protocol for alarms and events, and so on.

## Slide 12: Network Architecture
Internet
client.l4p server1.l4p
N
N
N
N
FieldPoint
PLC
Citadel
client.l4p server2.l4p
client.l4p
client.l4p
Citadel

## Slide 13: Network Security
Network access to your project controlled
  Read and/or write access to certain users limited
  Available at process, folder, and object level
Process security
  IP access grant/deny
  Proxy user designation
Notes: Lookout development security is modeled after Windows NT security but is supported for Lookout processes running on Windows 98/95 as well. Users with the ability to access processes or elements within a process are organized into groups. You can limit group and user access to processes, folders, and objects.
You can configure Lookout to grant or deny access to any computer operating at a specific IP address.
You can, if you choose, designate a specific local security account whose security level applies for any user accessing processes in your local instance of Lookout from another computer (or another instance of Lookout running on the local computer).

## Slide 14: Symbolic Links
Analogous to a pointer in C
Applications
  Multiplexing
  Abstraction
  Redundancy
Notes: The symbolic link in Lookout works very much like a pointer does in C. It is a reference to another Lookout object, folder, process, or computer. This reference is either fixed at runtime (static symbolic link) or dynamic (dynamic symbolic link).
The dynamic symbolic link takes a text variable as its input. This text contains a URL to the object, folder, process, or computer at which you want the symbolic link to point. By modifying this text variable at run time to represent different URLs, you can change what the symbolic link represents. By reading data through the symbolic link, it becomes a powerful multiplexing tool.
The symbolic link also serves as an abstraction layer. For example, say you need to write a client application that refers to a server, but you don’t know the machine name of the server. You can create a symbolic link in the client process called “servermachine” and have it point to some convenient machine for development. When the server machine name changes, you can just change the value of that symbolic link. In this same way, you can change machines dynamically in your process to implement very flexible redundant systems.

## Slide 15: Client Server Process Architecture
Separate control from GUI
  Only run processes that need to run
  Easier to maintain smaller processes
Your GUI is implemented once and run anywhere
Notes: Separating your control logic from your GUI is a matter of good design in any system, and Lookout is no different. Besides isolating critical from non-critical processes and thus minimizing the risk of serious bugs in your system, with this paradigm, you only run the processes that need to run at a particular time, conserving precious CPU time. It also encourages developers to develop smaller, more specialized processes that are easier to understand and maintain.
With this separation you implement client processes that are not in any way machine dependent so that they can run anywhere on the Internet. This design practice saves you the hassle of having to implement the same user interface multiple times.

## Slide 16: Web Client
You can export a Lookout client process to the Web
Lookout runs as an ActiveX control in Internet Explorer

## Slide 17: Aggregate Objects
You create your own objects from existing objects
Encapsulation
Reusability
Complexity is easily managed
Notes: With the aggregate object feature in Lookout 4.5 you create your own Lookout objects from existing Lookout objects. You define an aggregate object by:
1) Creating objects
2) Creating connections between those objects
3) Defining the datamembers of the aggregate object by choosing from the datamembers of the objects you've created
This object can then be instantiated multiple times like any other Lookout object. With this feature Lookout developers retain their process development skills in a library of acquired Lookout objects that can be reused or sold to others. It is also a powerful abstraction tool that helps you to understand complex processes.

## Slide 18: Lookout is SCADA made easy!