## Slide 1: FieldPoint™ Distributed I/O Hands On
Aaron Gelfand
FieldPoint Product Support Engineer
Wed Aug 16
10:15-11:30 a.m., 12:00-1:15 p.m., 1:45-3:00 p.m., 3:30-4:45 p.m.
Exhibit (3F)

## Slide 2: Overview
Introduction
Isolation
Wiring techniques
Power-up settings
Watchdogs
Ethernet configuration
Sampling rates

## Slide 3: FieldPoint Isolation
Isolation per module
Channel to channel isolation only for discrete dual channel modules
2500-3000 Vrms isolation
250 Vrms safety isolation, working voltage
No electrical connection between backplane and I/O circuitry
Notes: The isolation rating is the maximum voltage differential that can occur between the common terminal on the terminal base (the input circuit's ground level) and the common in the backplane of the module (the network module's common level) without causing damage to the circuitry.
Safety Isolation (or working voltage) is the maximum voltage differential (per safety isolation specifications) that can be sustained between the common terminal on the terminal base (the input circuit's ground level) and the ground in the backplane of the module (the network module's ground level) while still allowing accurate measurements and safe working conditions for human operators.

## Slide 4: FieldPoint Isolation Wiring
Inputs/Outputs optically isolated from control circuitry
Each base has Vsupply & Common linked to I/O circuitry (non-isolated side)
Cascading power (by jumpering V or C terminals) defeats isolation
Colors represent different potentials
Notes: Each base provides a common and a Vsupply. The common and Vsupply are used for power and referencing of the I/O signals only, they do not reference to the common or power supply of the FieldPoint control circuitry. One common technique is to jumper the Vsupply and Common from module to module. This allows a single power supply to power both the modules and their outputs, but defeats isolation and protection of the system. Input modules do not need the Vsupply or common wired although it is recommended to wire the common to the common of the incoming signals (assuming a common ground for the signals). Most output modules do require that the Vsupply and common be wired and powered.
A FieldPoint bank can have up to 10 separate, electrically-isolated grounds. The network module has a common from the supply that is powering it. This is electrically connected to the backplane's ground. Each terminal base has a common terminal that is used for the isolated side of the input/output circuitry. With installations that do not need isolation, customers frequently link the power connections (common and Vsup) of one terminal base to the next, all the way down the line to the network module. This allows outputs to be powered by the same supply (assuming the supply can provide enough power to meet the demands of the modules AND the analog output currents). Doing this will result in a single ground being established for both the backplane and the input/output circuitry. This defeats the isolation of the modules. For the best isolation, do not connect the power supply terminals of the terminal bases together. Power any output modules independently. For medium isolation, use one power supply for the network module and one for the output modules (establishing two independent grounds - one for the backplane and one for the output modules).

## Slide 5: Cascading Power Current Limits
• Cascading power (by jumpering V or C terminals) defeats isolation
Notes: If you decide to cascade the power and common of multiple I/O modules, you need to take into consideration the total current that will be conducted down the base terminals. If the total current is more than 10 amps, you need to wire each power and common from trunk voltage and common lines rather than cascading from module to module.

## Slide 6: Wiring Devices – Current Limits
It < 3A
It > 3A
Notes: If the total current flowing through all the channels on a module to a common return wire is less than three amps, then a single wire may be used as a collective return path to a single terminal. However, if the total current is greater than three amps, use separate wires to connect each device to separate terminals on the base.

## Slide 7: Sample System

## Slide 8: Power Up Settings
User defined or factory default
  Ranges
  Attributes
  Values
2 ways to configure
  Channel configuration window
  Snapshot function
Notes: A module can power up in two modes – factory default and user specified. In each mode, the ranges, attributes, and values (for output modules) are automatically configured each time the FieldPoint bank powers up. The factory default mode has all outputs turned off or set at a value of zero.

## Slide 9: Watchdog
Two Watchdogs
  Power up
  Programmable
Network module watchdog operation starts:
  first command received (FP-1000/1001)
  first subscription received (FP-1600)
Output module watchdogs:
  Enable (immediate)
  Enable on use (first read/write to module) (not supported for FP-1600)
The network module watchdog must be enabled for I/O module watchdogs to work
Notes: The watchdog is a communication monitor, it will time out when the period of time (watchdog delay) for periodic message of normal operation from the client has elapsed. Whenever the watchdog delay is exceeded, the FieldPoint output modules go into the watchdog state. When in the watchdog state, each channel of the FieldPoint output modules is set to its watchdog data value. This allows you to place your FieldPoint outputs to a known state during system failure.
Probable reasons for time-outs include
Disruption in communications
Computer failure
For network modules, you can set the watchdog to enable on power-up or on first use. Network modules must power cycle for the watchdog to take effect if you set it for power-up mode. For I/O modules, if you choose to enable the Current Watchdog, the watchdog timer is enabled immediately after you click on the OK button in the Device Configuration dialog box. If you choose enable on use, the watchdog timer enables only after you send the first read or write command to the FieldPoint hardware. The network module watchdog must enable for I/O module watchdogs to enable.

## Slide 10: FP Explorer – FP-1600 Configuration
Network settings
  IP address (required)
  Subnet Mask (required)
  Gateway IP (optional)
  DNS server IP (not used)
  Time server IP (optional)
  Comment (optional)
Firmware
Notes: On the FP-1600 properties screen, you configure a FP-1600’s network settings. You can assign it an IP address, a subnet mask, a Gateway IP, a Time server IP, and a comment for the device. The comment will show up when someone browses the network, so it is useful for identifying the device.
The IP address and subnet mask are used as the primary configuration for the FP-1600. The FP-1600 should be located on the same subnet as the computer that will act as the time server and the computer that is used for configuration. The subnet is determined by logically “AND”ing the bits of the Subnet mask with the IP address.
The Gateway IP is the address of a machine that connects the local network to the Internet or to separate network portions.
The DNS server IP, currently not used as a FP-1600, will try not to identify computers through DHCP.
The Time Server IP is the IP address of the computer on the network that is acting as a Time Server to allow synchronization of the onboard clocks on the FP-1600. In general, all 1600’s associated with a particular network have the same time server. The 1600, if rebooted and without access to a time server, starts with a time stamp that is 0000 GMT March 25, 1998.
The comment field can be used to identify a module on the network.
Use the Firmware button to check the current revision of the FP-1600 and to update the firmware if desired.

## Slide 11: Sampling Rates - Serial
Two Factors
  Data throughput
    Utility FP16_rates (.vi, .xls)
  All channel update rate
Notes: There are two issues to consider when dealing with FieldPoint sampling speed - channel update rate and data throughput rate. Whichever of these is slower is the limiting factor. The channel update rate is how fast you can read data from the channels (sampling) and is found in the catalog for the particular module you are using. The data throughput rate is how fast you can get the data through the network module to the computer. The channel update rate is a function of the FieldPoint Module.
The update rate depends on the particular type of module. For examples, FP-AI-100 modules update at a rate of 2.8 ms. The update rate of the FP-AI-110, however, depends on the filter setting. It updates the channels every 0.173 seconds with the 500 Hz filter setting (regardless of how many channels you read; all the channels get updated every 0.173 seconds whether you read them or not). On the 60 Hz filter setting it updates every 1.23 seconds, and on the 50 Hz setting it updates every 1.47 seconds.
Say the benchmarking utility says you can acquire one channel of an analog input module in 17 ms (data throughput rate). If you tried reading the data of an FP-AI-110 with a 500 Hz filter at this fastest rate, the computer would get the same data 10 times in a row (173 ms divided by 17 ms) before the I/O module updates the data. On the other hand, if you read one channel of the FP-AI-100 (which updates its data every 2.8 ms) every 17 ms the computer would only see every sixth sampled data point from the module.
The important thing to remember is that the sample rate of the I/O module and the throughput rate of the network module are completely independent. Sometimes (depending on system) the I/O module will sample data faster than you can read it and sometimes you'll be able to read the data faster than it can be refreshed. There are no built-in features to prevent the loss of data (due to overwriting prior from update), although several of the language interfaces allow you to filter the same value to prevent it from being read multiple times.

## Slide 12: Sampling Rates – Ethernet
Three Factors
  Data throughput
  All channel update rate
  Rate of change of signals
Notes: There are three issues to consider when dealing with FieldPoint Ethernet sampling speed – data throughput rate, channel update rate, and rate of signal change. These factors combine to form the maximum sampling rate. The channel update rate is how fast you can read data from the channels (sampling) and you can find it in the catalog for the particular module you are using. The data throughput rate is how fast you can get the data through the network module to the computer. The FP-1600 automatically scans all subscribed channels and attempts to transmit any changed data. Thus, slow changing signals are not transmitted frequently freeing up network bandwidth for the faster changing signals.