## Slide 1: A Technical Survey of Industrial Networks
Jacob Kornerup, Ph.D.
R&D Group Manager
Wed Aug 16
10:15-11:30 a.m., 1:45-3:00 p.m.
San Jacinto (5B)

## Slide 2: Outline for Presentation
General networking concepts
Survey of industrial networks
  DeviceNet
  CANopen
  FieldBus
  PROFIBUS
  Ethernet
Conclusions

## Slide 3: Industrial Bus Hierarchy
Enterprise
Control
Fieldbus
Devicebus
Sensorbus
N
N
N
N
N
N
N
N
Fisher
Notes: Today, a full industrial bus hierarchy can contain several levels, connected via dedicated gateways. In general, devices at the bottom of the diagram have lower costs and lower functionality and devices at the top have higher costs and higher functionality.
CAN is an example of a sensorbus; DeviceNet and Profibus fall into the area of devicebus. FOUNDATION Fieldbus and Profibus are considered Fieldbuses. ControlNet and FOUNDATION Fieldbus are considered control buses, and various plant and enterprise-wide protocols running on Ethernet fall under the Enterprise category.
Note that even though FOUNDATION Fieldbus and the enterprise portions might share a common physical layer (Ethernet) and maybe several common layers of protocol (IP, TCP), there is likely a gateway between them to limit the traffic onto the control bus.

## Slide 4: Capability Hierarchy
Level of functionality
  Enterprise bus (Ethernet)
  Control bus (HSE, ControlNet)
  Fieldbus (Foundation Fieldbus, Profibus PA)
  Device bus (DeviceNet, Profibus DP, Interbus-S)
  Sensor bus (CAN, ASI, Seriplex, LonWorks)
Notes: A sensor bus is usually a high-speed, bit-level bus; the messages sent tend to be expressed as one or more bits and the messages tend to be very short for low-access latency.
In terms of software, sensor buses are extremely low level. CAN does not reach even layer two of the OSI model (it implements the MAC portion of data link, but not the LLC portion). This means there is no connection concept.
Device buses are also high-speed buses, but may have longer messages and more network software functionality. DeviceNet has an object model with different types of connections for configuration and I/O.
Fieldbuses are typically lower-speed buses, with longer messages and greater network software capability. FOUNDATION Fieldbus has a rich, extensible object model with several types of connections, providing higher-level functionality such as redundant master switchover directly in the protocol.
Control buses combine the high speed and low latency of the sensor bus with the high functionality and control of the fieldbus. HSE can be used to put the FOUNDATION Fieldbus control model onto a high-speed medium. ControlNet takes a similar approach, putting the DeviceNet object model onto a high-speed, deterministic network.

## Slide 5: OSI Network Model

## Slide 6: OSI Transport Layers
Layer 1 – Physical
  Encodes and physically transfer messages
Layer 2 – Data link
  Breaks up and reassembles messages
  Error detection and correction at the bit level
Layer 3 – Network
  Routing of Message Packets
Layer 4 – Transport layer
  Split data into messages to be transported

## Slide 7: OSI Application Layers
Layer 5 – Session layer
  Establishes sessions between machines
Layer 6 – Presentation layer
  Convert data formats between application representations and network representations
Layer 7 – Application layer
  Provide a uniform layer that abstracts the behavior of the network

## Slide 8: Typical Industrial Networks
Notes: Layers 3 through 6 are typically not used in most industrial networks.

## Slide 9: Choosing an Industrial Network
Application requirements
  Physical layer suitability
  Network capabilities
  Integration with existing equipment
  Speed and timing requirements
  Availability of components
Cost
  Installation, device, training, maintenance

## Slide 10: DeviceNet – Physical Layer
  DeviceNet is an open standard (ODVA)
  CAN for communication layer
  125, 250, or 500 kbps
  Up to 64 devices per network
  Differential signaling
  Power available on bus
  Up to 500 m at 125 kbps
  11 bit arbitration ID
PC
Trunk
Drop
Notes: A DeviceNet network can communicate at 125, 250, or 500 K bits per second. Slower baud rates imply longer cable lengths (500 m trunkline at 125Kbaud, 100 m trunkline at 500Kbaud). 125Kbaud is popular in Manufacturing Automation applications, whereas 500Kbaud is popular in Semiconductor Manufacturing.
DeviceNet cables and connectors include 5 signals: CAN high and CAN low (differential signaling), power and ground (for self-powered devices), and a shield (to improve noise immunity).
DeviceNet requires termination resistors at each end of the main trunk line.

## Slide 11: DeviceNet – Application Layer
Types of communication
  Explicit messages
  IO connections
Types of IO connections
  Polled
  Strobed
  Change-of-state
  Cyclic
Notes: I/O connections provide cyclic and event-driven communication for use by run-time control algorithms. DeviceNet also supports peer-to-peer communication, in which no clear master exists in the system (all devices are equal). Since most devices only implement slave communication, peer-to-peer systems are uncommon today. Note that “master/slave” does not imply that only the master can initiate communication. It is possible for a slave device to send an unsolicited I/O message to the master.
Polled: Master sends request to a single slave, then that slave responds.
Strobed: Master sends a broadcast message. All strobed slaves detect this message simultaneously, then each responds with its sensor data. Used for simple sensors like photo sensors and limit switches.
Change-of-state: Slave can send a message to master whenever it detects a change in its data. The master can send a COS message as well.
Cyclic: Slave can send a message to master periodically (or vice versa).
Not all devices support all I/O connection types. Some only support polled or strobed. Also, each slave can only one I/O connection of each type. For example, it is not possible for a slave device to support two polled I/O connections.

## Slide 12: DeviceNet Continued
Object model
  Class
  Instance
  Attributes
  Services
Electronic data sheets
  Some devices are self-describing
Notes: DeviceNet uses object concepts to provide commonality among different devices. For example, every DeviceNet device provides an Identity Object (class = 1, instance = 1). This object’s behavior identifies the device and controls overall operation of the device. For example, the Identity Object provides attributes for Vendor ID, Product Name, Serial Number, and so on. The Identity Object also provides the Reset service, used to reset the entire device to its power-on state. Since all device vendors are required to provide this object, PC-based software can easily identify/reset any device.

## Slide 13: CANopen – Physical Layer
  Open standard (CiA)
  CAN for communication
  10kbps to 1 mbps
  30 m – 5 km
  Up to 128 devices per network
  11 or 29 bit arbitration ID
PC
Trunk
Drop
Notes: Unlike Devicenet, CANopen supports up to 1 mbps data transfer and 29 bit arbitration IDs.

## Slide 14: CANopen – Application Layer
Types of communication
  Real-time data
    Event-driven
    Polling
  Configuration parameters
  Time synchronization
Device profiles
  Guidelines for designing “like” devices
Notes: The CANopen protocol defines several methods for transmission and reception of messages over the CAN bus. These messages are referred to as communication objects. Synchronous data transfers allow network wide coordinated data acquisition and actuation. Synchronous transfers are supported by predefined communication objects (Sync Objects transmitted on a cyclic time period and Time Stamp Objects). Asynchronous or event messages may be sent at any time and allow a device to immediately notify another device without having to wait for a synchronous data transfer to take place. The content of both synchronous and event telegrams (Process Data Objects) may be dynamically configured at boot up by the machine controller. Although CAN is restricted to transfers of a maximum of eight data bytes within one telegram, data transfers larger than eight bytes are also provided for by the protocol (Service Data Objects).
CANopen uses the concept of device profiles, which aids systems integration and device standardization. By conforming to the guidelines contained in a CANopen device profile two independent manufacturers can produce standardized devices. This approach allows a system integrator to decouple himself from a specific device manufacturer. This allows networks of devices from independent manufacturers to be constructed without having to write specific software for networking each device together. Both optional and manufacturer specific functionality can also be defined for a device using the CANopen profiling mechanism. By defining mandatory device characteristics, basic network operation is guaranteed.

## Slide 15: Profibus and FOUNDATION Fieldbus Physical Layer
Profibus PA and FOUNDATION Fieldbus
  Standard is IEC 61158
  31.25 Kbps
  Up to 32 devices per segment
    More with repeaters and bridges
  Differential signaling
  Power available on bus
  Up to 1900 m
    More with repeaters
PC
IS
Barrier
Notes: The physical layers of these two standards are identical. Each Profibus and FOUNDATION Fieldbus segment can contain 32 devices. A given segment can contain up to four repeaters, allowing for (4+1) * 32 = 160 devices maximum per logical segment.
If most devices are bus powered, which is typical, DC power limits the number of devices per segment from 10 to 20, depending on the devices and cable lengths. Bandwidth at 31.25 kbps is another limiting factor, depending on the speed of control or human-machine interface (HMI) updates required.
In intrinsically safe (IS) applications, the number of devices per segment is typically 4 to 6 because of power constraints. The IS barrier is installed at the start of the IS area, and limits the amount of power available on the bus.

## Slide 16: Fieldbus – Application Layer
Each device consists of blocks
  Resource block - characteristics of device
  Function block(s) - the control and I/O behavior
    Execution can be scheduled deterministically
    Execution is synchronized with communication
    Device may support dynamic instantiation of FBs
  Transducer block(s) - local I/O connections
Electronic data sheets
  Not on devices
Interoperability among vendors
Notes: Function Blocks are the core components with which you specify the behavior of a control system. During system configuration, the inputs and outputs of functions blocks are interconnected to define control strategies. The execution of these function blocks, as well as the communication of data between them over the fieldbus, can be precisely scheduled. This is a key capability of FOUNDATION Fieldbus – control loops are executed directly over the network. The Function Blocks themselves reside in the devices but the overall scheduling of execution is specified and executed across the network.
Through function blocks and device descriptions, Foundation fieldbus enables products from different manufacturers to work together in a full-function, integrated manner.

## Slide 17: PROFIBUS – Application Layer
Communication
Logical token ring
  Master/slave paradigm
    Real-time data, accessed by polling
Electronic data sheets
  Fixed device profiles, not vendor definable
Simple and fast
Notes: Communication is permanent and cyclic – the master talks with every slave configured and after exchanging data with the last slave it starts again. The master configures the slaves prior to the data exchange – the amount of data for the data exchange is part of the configuration. Only the master that parameterized and configured the slave can write the output data of the slave. A so-called class 2 master (service device) can read the output data of a slave. Extensions offer the possibility of acyclic data transfer between poll cycles – this can be used for downloading a new parameter set to instruments, for example.
Profibus has committee-defined profiles that describe the exact functionality provided by each object. The profiles are rigid and not extensible by device vendors.

## Slide 18: DeviceNet – Customer Benefits
Interoperability of devices
  Photo eye from list of conforming devices
    Allen-Bradley
    Cutler-Hammer
De facto standard in the U.S. semi-conductor industry
Widely used in the U.S.
NI provides DeviceNet connectivity

## Slide 19: PROFIBUS – Customer Benefits
Simple and fast
Widely used in Europe
  Semi-conductor industry
  Industrial Automation
NI provides PROFIBUS interface cards and conformance testing software

## Slide 20: Migration to Ethernet
DeviceNet  EtherNet/IP
  Specification to be released later this year
PROFIBUS  “PROFIBUS on Ethernet”
  Announced in Q2 of 1999
Fieldbus  HSE
  Announced in 1998
Notes: Many of the serial/bus-based protocols are migrating to Ethernet. This is done by packaging and sending the protocol messages over TCP/IP.

## Slide 21: Integrating with Ethernet
Notes: There is a strong pull towards integrating the industrial networks with more enterprise-wide networks, which for all practical purposes means Ethernet. This is achieved by using gateways between the Ethernet and the industrial networks.

## Slide 22: Physical Layer – Ethernet
10 Mbps, 100 Mbps
Virtually unlimited devices per network
  hubs, switches and routers allow for hierarchical networks
No bus power
Everywhere in the enterprise
  making it on to the factory floor
Notes: Similar to most networks, the topology of an Ethernet network gets complicated as the number of devices increases. Switches, hubs, and routers are used to create separate collision domains where devices are more isolated from the unwanted traffic of other domains.

## Slide 23: Ethernet Protocols
Ethernet describes a link and physical layer

## Slide 24: National Instruments Networking
NI’s industrial Ethernet protocol
In the following NI products
  Lookout™ 4.0
  FieldPoint™ FP-1600
  LabVIEW™ 6i
Designed to scale to large IO counts
  One PC monitoring over 50,000 IO points using Lookout
Built on top of UDP/IP
Event-driven
Fast, but not highly deterministic

## Slide 25: Sharing the Network
Internet
N
N
N
N
PLC
Citadel
server2
Web client
client1
Citadel
server1
client2
FP-1600
Gateway
Industrial
network
Notes: This slide illustrates the networking and client/server capabilities of National Instruments products. It shows a typical application with multiple servers and multiple clients. The NI protocol shares the network with other TCP/IP protocols, such as HTTP and FTP. The topology can be chosen in such a way that speed and determinism can be estimated. Any real-time data being read by a server can be accessed by any client on the network.
Citadel is National Instruments historical database. Any real-time data being logged historically to any Citadel database can be accessed by any client on the network. A server can log data to a Citadel database on a different machine.
By adding gateways to this network it is possible to integrate the industrial networks. Data from the industrial network can then exposed to the enterprise through the NI network protocol or OPC and viewed on any client, including web clients.

## Slide 26: NI Networking Features
Browsing
  What devices are on the network
Security
  Based on Windows NT security model
Historical Logging
  Optimized for logging across a network
Alarms and Events
OPC connectivity through Lookout
Notes: The NI browser protocol is used by our IA products to implement tree views, so a user can browse a set of machines, the Control Environments (CEs) on those machines, the processes running on those CEs, and the folders, blocks, and data items that exist in those processes. When an item is selected, you can use its full pathname (URL) to subscribe to that item’s real-time or historical data. The protocol handles hierarchical namespaces with no inherent limitations on tag lengths or tree depth.
Security is supported on Windows NT/9x. Access rights at the level of individual tags or channels.
When reading or logging historical data, a cache is maintained on the client machine. Data is passed between server and client in chunks using the native, compressed data format of Citadel. This minimizes network bandwidth usage, and allows clients to be responsive.
If the connection to the server is temporarily lost, the local cache continues to buffer the data so that no data is lost, provided that the connection is reestablished before the local computer runs out of memory. Quality is logged along with data. Each client can access multiple servers and each server can service multiple clients.
Alarms and events are stored in Citadel and are available from the moment they are generated to the moment they are aged out or explicitly removed from Citadel.
An alarm consists of three events – activation, deactivation, and acknowledgement. Deactivation and acknowledgement can occur in either order. Because these three events can occur over a long period of time but need to be associated with each other, it made sense to use a protocol and storage mechanism different from that used for historical data. Alarms and events are categorized by area as well as priority. A client, such as an alarms and events browser, can subscribe to a filtered subset of the alarms and events.

## Slide 27: Conclusion
Many choices among industrial networks
Choice depends on:
  Which devices needs to be connected
  Existing infrastructure
  Required response time
  Level of determinism
  Connectivity to the enterprise
Most protocols are evolving toward Ethernet