## Slide 1: Distributed Measurement Systems
Garritt Foote
Industrial Hardware R&D

## Slide 2: Topics of Discussion
Uses for Ethernet in DAQ and I/O systems
Performance of Ethernet
National Instruments networking options
Ethernet on FieldPoint™
Notes: Much of the discussion today will be a general overview of the characteristics of Ethernet systems that relate to the usability and performance of I/O and Data Acquisition (DAQ) applications.
We will start with a brief discussion of the benefits that Ethernet can bring to DAQ and I/O systems. Next we will cover the performance characteristics of an Ethernet network and discuss different configurations of networked DAQ or I/O systems. Then we will discuss some of the different options that National Instruments provides for networked access to DAQ or I/O devices and how these tools can be used in the various networking configurations.
National Instruments has actively been bringing networking technologies to the concept of virtual instrumentation, and covers many topics of distributed virtual instrumentation in other sessions at NI Week 2000. For more information on networking and distributed measurements try some of these sessions.

## Slide 3: Why Ethernet for I/O and DAQ?
Many connectivity options
  multiple devices connected to multiple PCs
  connection to the Internet
Ethernet is everywhere
  the de-facto networking standard
  growing acceptance for industrial use
  supported by PCs and Windows
Performance at a low cost
Notes: Ethernet provides a fast, reliable, low cost network. As the de facto networking standard, Ethernet is well developed for a variety of networking and performance needs. Ethernet makes it easy for multiple I/O and Data Acquisition devices to share data and information with multiple PCs. Ethernet also makes it easy to manage the flow of information between the control network and other networks that support enterprise wide connectivity to business systems. Tying Ethernet I/O and Data Acquisition devices into the Internet brings the possibility of having data available anywhere, anytime.
The widespread use of Ethernet has made a large variety of products available from a number of vendors, and has driven the costs of Ethernet solutions to very attractive price/performance points. With this widespread use also comes widespread knowledge – not only are there a large number of reference texts on the subjects of Ethernet and network utilization, but most companies using PCs are likely to already have in-house experience in the field.

## Slide 4: Ethernet – For Connectivity
Multiple clients (PCs) can share access to multiple devices
Direct connection to the Internet
N
N
N
N
N
N
N
N
Notes: Perhaps the most common benefit of using Ethernet is in networked applications, where multiple PCs need to share access to the data from one or more I/O or DAQ devices.
In many applications, there will be different levels of access to the I/O signals, from continuous real-time direct access to occasional supervisory access. As a common networking platform across many networks, Ethernet can provide a single architecture for all these application ‘domains’.
Through the use of protocols such as IP, Ethernet can provide easy access to the Internet, opening up a wide range of possibilities for networked DAQ and I/O applications.

## Slide 5: Ethernet is Everywhere
Ethernet is the de-facto corporate information and manufacturing networking standard
Supported by PCs with Windows NT/9x and many control devices
Low cost
Easy to install, use, and maintain
Well understood
Notes: Ethernet has traditionally been used as the business information backbone and is pretty much the de-facto network installed in many companies today. Many corporations that use Ethernet for business systems can leverage their existing infrastructure for both business and manufacturing automation systems. Ethernet and IP is one of the most widely used networks worldwide. This ubiquity of Ethernet provides many benefits including:
Ethernet products are commercially in very high volumes. Ethernet is built onto the motherboard of many PCs and cost less than $50 (US). Windows NT/9x comes with built-in support for many Ethernet boards and IP.
Ethernet is rapidly becoming the de facto industry standard high speed communication backbone for many industrial control systems and devices.
Since Ethernet is already used for sharing information between business application, it will make it easier to integrate and share manufacturing information.
Most businesses already have the in-house expertise in network administration and Information Systems to design, install, and maintain even complex Ethernet systems.

## Slide 6: Anatomy of an Ethernet Network
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
N
To corporate
backbone
Local traffic
Local traffic
Traffic routed to destination
Switching hub
Repeater hub
Switching hub
Segmented collision domain
Repeater hub
Notes: In the most common form of Ethernet networks, devices are connected to hubs in a star network. Simple repeater hubs cause all of the devices to appear to be connected together; any time one devices transmits data, all of the other devices receive the data. A set of devices interconnected in such a manner is referred to as a “collision domain”, since two or more devices that attempt to send messages at the same time cause a collision.
To prevent these collisions from degrading performance, switching hubs may be used in place of repeater hubs. Switching hubs only pass messages to the devices for which the messages are intended. Thus, collisions only occur when two or more devices attempt to send messages at the same time to the same destination.
For a more complete discussion of the workings of Ethernet and the internet, refer to the presentation, “How does the Internet Work”, by Dr. Guy Vachon. This presentation will discuss performance characteristics of Ethernet networks and methods of improving performance.

## Slide 7: Collisions on Ethernet
Ethernet devices wait to transmit until they sense the network is clear (Carrier Sense)
Node 1
Node 2
Node 1 starts transmitting
Node 2
starts waiting
Node 2 senses a clear network and starts transmitting
Notes: Ethernet works on a principle of Carrier Sense and Collision Detect. Since multiple devices may all share the Ethernet and may all be transmitting at any time, devices monitor the network and wait until it is clear before transmitting data. In the example on the slide, the second node is ready to send its packet of data but it senses that the network is busy with traffic from the first node. The second node waits until the first node finished, then it starts transmitting. The delay experienced by the second node’s data packet is proportional to the length of the first nodes packet, and the frequency with with the delay occurs is proportional to the percentage of time that the network is busy.
Summary:
Shorter packets provide proportionally shorter carrier sense delays, and less total data traffic provides proportionally fewer occurrences of these delays.

## Slide 8: Collisions on Ethernet
BUT, when two devices start transmitting at the same time, a collision occurs
Node 1
Node 2
Node 1 starts transmitting
Node 2 starts waiting
Nodes 2 and 3 both sense a clear network and start transmitting
Node 3
Node 3 starts waiting
Collision
Notes: When two Ethernet devices start transmitting at the same time, their messages collide. The “same time” really means within the time it takes for the electrical signal to propagate along the wires, and so short cable lengths provide a very small window of opportunity for “same time” collisions. However, these collisions can still occur when there are two nodes waiting for the line to clear. In the example on this slide, nodes 2 and 3 are both waiting for node 1 to finish transmitting. When these two nodes sense a clear carrier, they both start transmitting at the same time and cause a collision. Collisions are a normal part of Ethernet messaging, and devices are equipped with Collision Detect. In this example, nodes 2 and 3 will detect the collision, and they will each stop transmitting and try again after a random amount of time. If this retry also fails, they will each wait another random amount of time and try again. This process repeats up to 16 more times before the nodes give up and report an error.
This collision detection mechanism is often pointed to as being the cause of non-determinism in Ethernet. And it is true that the total delay experienced because of a collision is a random function. However, the next slides will show that the probabilities of significant delays can be made exceedingly small. For example, the probability that nodes 2 and 3 in this example will exhaust their 16 retry limit is 1 in 1035.

## Slide 9: Probability of Collisions
Notes: For long cable distances and short bursts of information, the probability of collisions is dominated by the random starting of packets in the “same time” window defined by signal propagation. As the “same time” window gets shorter, the probability of a collision is determined by the likeliness of having multiple nodes waiting for the line to clear, as in the last slide. This chart indicates the probabilities of any given packet causing a collision in this manner. It shows different cases in which multiple nodes randomly send packets at the indicated average rates.
The graph shows that the probabilities of collisions roughly increase with the square of the packet size, with the square of the rate of packets, and with the square of bandwidth of the network. It also shows that keeping the number of nodes to a minimum has a significant impact on the probability of a collision.
Summary:
Shorter packets, less frequent packets, few nodes, and fast Ethernet can all make significant improvements in reducing collisions

## Slide 10: Effect of collisions
Max delay (ms), 10 Mbs
Max delay (ms), 100 Mbs
.3
.03
.7
.07
1.5
.15
3.1
.31
6.3
.63
13
1.3
26
2.6
51
5.1
Notes: The next logical question is, how bad are collisions? As described earlier, the length of delay caused by collisions is based on the colliding nodes waiting a random amount of time and then retrying to send their data packet. The number of retries required before one of the messages gets through is a random number shown in this chart. As the chart shows, the probability of requiring more than 5 retries is less than one in a million collisions. The delay encountered by these 5 retries is also a random number, but is no more than 6.3 milliseconds for a 10 Mbs Ethernet, and no more than 0.63 milliseconds for a 100 Mbs Ethernet. Of course, the node which “loses” this decision to send its data is back in the carrier sense mode and has to wait an additional delay while the “winning” node sends its data packet
Summary:
Delays caused by collisions are on the order of milliseconds, and are even smaller when 100 Mbs Ethernet is used.

## Slide 11: Maximizing Ethernet Performance
Use fast Ethernet
Minimize nodes in each collision domain
Send short, efficient packets of data
Send packets as seldom as necessary
  Ethernet performance can be made a non-issue for many applications
Notes: The keys to maximizing Ethernet performance can be summarized as:
Use Fast Ethernet
Going from 10 Mbs to 100 Mbs Ethernet reduces the waiting time for a clear channel by a factor of 10, and reduces the probability of a collision caused by multiple nodes waiting for a clear channel by a factor of 100, and reduces the waiting time caused by collisions by a factor of 10.
Use no more nodes in each collision domain than is necessary
Fewer nodes means a lower probability of waiting for a clear channel, and lower probability of collisions. Use switching hubs to limit collisions domains to devices which will normally be communicating with only each other. A single PC getting data from several DAQ devices can stay within a single collision domain, since a switching hub will just pass all the data from the DAQ devices to the PC anyway.
Send short, efficient packets of data
Send only the data you are interested in; don’t monitor unused channels, use event-driven protocols that send only changes in data.
Send packets as seldom as necessary
Again, using an efficient event-driven protocol can minimize the packet rate.

## Slide 12: Networking Your Measurements
Key to performance is your network setup
  Computers and I/O devices need to be able to handle all this reliable networked data
  Network setup should also be tolerant of casual or non-critical network accesses
Notes: Now that we’ve seen how to maximize the performance of an Ethernet network, the next step is to make sure that the computers and devices on the network can take handle all of the tasks given to them. Much has been written on the reliability, determinism, and susceptibility to overloading of an Ethernet network, but in many applications the weak link is not going to be the network itself, but will be the devices and computers on the network. Particularly in a poorly constructed or poorly used setup, devices may be overwhelmed with requests for data if too many computes have direct access to them, or computers may be overwhelmed with data from devices or requests for data from other computers.
The key to a reliable system, of course, is to limit the burden placed on critical devices over the network, and to understand to behavior of devices and computers when they do get overwhelmed.
For example, if you want a Web server interface into a control process to allow anyone can with a Web browser to look at the data of the process, consider the situation where many casual Web browsers are looking at the data. If they all directly access the I/O devices of the process, they may take up so much of the I/O devices time that the device cannot keep up with the control of the process.

## Slide 13: Complete, Direct Access
Several PCs directly access each of several I/O devices
  I/O devices stay busy with each PC
  Best when all PCs need direct access to I/O
  Not as appropriate when PCs are used for casual or restricted access to I/O devices
N
N
Notes: In some cases, it is preferable to have multiple computers and multiple I/O devices directly accessing each other as this slide shows. This does not necessarily mean that all of these computers and devices are on the same collision domain, just that the computers and devices can exchange information directly.
This system has the advantages of being simple, inexpensive, and lacking any single bottleneck. Every device or computer is a peer on the network, so there is no reliance on a single component. For this reason, this type of network is particularly well suited for applications requiring redundancy. One of the computers could act as a primary controller, with the other computers acting as backup in case of faults.
The potential drawback to such a system is that every device has potential to need to devote some resources towards communicating with each computer. If one of the computers was performing critical operations with one of the devices, than steps would need to be taken to ensure that the other computers and devices did not interrupt either the critical computer or its critical I/O device.

## Slide 14: Access Via Primary Computer
One PC control access to I/O devices
  I/O devices only need to expend communication resources on one PC
  Single PC controls access to devices
  Allows custom viewpoints
  Does not require networked I/O devices
N
N
Notes: Using a single PC as a gateway between devices and other computers isolates those computers from the devices. This way, the I/O devices have a limited set of tasks to perform, as they only need to communicate with a single PC. In addition, that PC can provide a customized viewpoint to the data. For example, that PC might serve a number of Web pages customized for particular applications, showing not only raw data but processed or analyzed data. In addition, the serving PC can provide data from both networked and non-networked I/O devices.
In many applications where a Web interface to an I/O product is desired, this type of system is going to be the most effective. LabVIEW and Lookout are both able to serve up Web pages of their front panels showing an arbitrary, application-specific view into the of the I/O system. In many of these cases where a Web interface (especially for casual viewing) is desired, a customized view is much more appropriate than a view of raw I/O points.
The potential drawback to this system is that if the serving PC is required to gather, store, analyze, or send data to the I/O devices, having arbitrary or unlimited access from other PCs may overwhelm the serving PC, preventing it from having enough bandwidth to reliably handle its critical tasks.

## Slide 15: Access Via Server Computer
One PC control access to I/O devices, second PC provides network access
  I/O devices and controlling PC are free from networking burdens
  Allows for critical control and casual monitoring
N
N
Notes: Using one or more computers to control access to I/O devices, and a second computer to handle networked interfaces, allows for full isolation of critical monitoring, controlling, and analysis tasks from non-critical casual or supervisory monitoring and control tasks. In this scenario, the primary computer still controls access to the I/O devices, providing these devices with a bound set of requirements, but that primary computer is also limited in its requirements by only needing to communicate with a secondary computer which handles all unbounded accesses from other networked users. This way, even if the secondary serving computer becomes temporarily overburdened trying to handle networked accesses, the primary computer is not adversely affected by the additional load.

## Slide 16: Ethernet Options for I/O and DAQ
RDA- Remote Device Access
  DAQ boards as shared resources
OPC/DCOM
  OPC servers use Microsoft’s DCOM
Application Software
  NI Software Packages have networking, web tools
Direct Connection
  Ethernet-to-GPIB and -Serial
  Ethernet FieldPoint
Notes: The following is a list of the networking technologies in National Instruments products that enable Ethernet based I/O or Data Acquisition.
The Remote Device Access (RDA) feature of National Instruments-DAQ provides a completely seamless method of calling a DAQ VI or CVI Easy I/O DAQ function remotely. RDA is specific to DAQ.
OPC (OLE for Process Control) is an industry standard device interface specification that provides interoperability between I/O devices and application software packages. It uses Microsoft’s DCOM technology to extend the interface across a (Microsoft) network.
National Instruments provides a number of networking and internet tools in its software packages, including e-mail, FTP and Web tools; a real-time protocol used by Lookout and FieldPoint; and our DataSocket technology.
National Instruments also provides direct connections from devices to the Ethernet with our Ethernet interface for the FieldPoint distributed I/O family, and with our Ethernet-to-GPIB and Ethernet-to-Serial converters.

## Slide 17: RDA – Remote Device Access
Remote Procedure Calls share DAQ resources
Similar to mapping network printers, drives
DAQ devices on one PC become “virtual” devices on networked PCs
Physical DAQ Board
RDA
“Virtual” DAQ Board
Notes: RDA is a feature of NI-DAQ software that allows a physical DAQ board in one PC to be logically mapped across the networked to another PC. This networked PC then “sees” a virtual DAQ board which can be accessed and controlled through NI-DAQ software as if it were locally available. This method is a completely transparent method of executing DAQ VIs and LabWindows/CVI Easy I/O DAQ functions on a remote station. No source code changes are required and no porting is required, and so there is no learning curve.
RDA is a good choice for implementing the remote DAQ part of a networked application. It is easy to send control data and get indicator data from a remote station. The calling overhead is low and the throughput is good. RDA might be used alongside one of the other techniques for performing non-DAQ functions on the remote station.

## Slide 18: OPC – OLE for Process Control
Industry standard interface
DCOM for access over Microsoft networks
Supported with NI-DAQ™, FieldPoint™, BridgeVIEW™, Lookout™, and DataSocket™
DAQ Board, FieldPoint, or Software app
DCOM
N
N
N
N
OPC
OPC
NI Servers
Any Client
Control Panel
Flow
Pressure Alarm Conditions
STOP
Temperature
Notes: OPC (OLE for Process Control) is an industry standard device interface specification that provides interoperability between field devices such as FieldPoint and application software packages. Both FieldPoint and NI-DAQ provide OPC servers which can communicate with any OPC client software. BridgeVIEW, Lookout, and DataSocket (which can be used from LabVIEW and Measurement Studio) are all OPC clients. (BridgeVIEW and Lookout are, in addition, capable of being OPC servers).
Because OPC is based in part on Microsoft’s DCOM (distributed component object model), it is possible for an OPC client on one computer to access FieldPoint hardware connected to the serial port of (or DAQ boards attached to) another computer if the two computers are networked together. The use of DCOM makes the network connection between the computers transparent to the OPC client’s access to the FieldPoint or DAQ hardware.
The FieldPoint OPC server is an out-of-process server, which allows multiple applications to access the FieldPoint devices. For example, you could have a Lookout application running on a computer directly connected to a FieldPoint system using the OPC server, and at the same time have access to the FieldPoint system from a BridgeVIEW application running on another computer over the network.

## Slide 19: Application Software
NI software packages have networking and internet tools available
Ideal for Web interfaces
  Provide useful data to any PC with a browser
Any Device
Internet
N
N
N
N
NI Software
Notes: Our application software, including LabVIEW, Measurement Studio, BridgeVIEW, and Lookout, provide a variety of networking and internet features. By using a PC running such software, that PC can become the network interface for the DAQ or I/O application. This can be particularly beneficial for many Internet applications where the raw measurement or control data is not meaningful enough to be available on a network. Software on the PC can interpret the data and present a useful view to the system over (for example) the internet as a Web page.
Our networking and internet tools offerings include:
DataSocket server functions in LabVIEW and Measurement Studio provide a simple means of sharing data between applications, whether they are on the same computer or networked computers. The DataSocket interface also can be used to access data shared between Lookout applications. Lookout allows any data member to be shared across a network or within an application with equal ease, using a real-time protocol described in the next slide.
VIServer is bundled with LabVIEW and provides a powerful, high-level tool for calling any VI remotely.
The Internet Toolkits for LabVIEW and LabWindows/CVI are purchased as add-ons and provide tools for creating email and FTP clients, and more. LabVIEW and Lookout have built-in Web server capability.

## Slide 20: Event-Driven Protocol
Efficient publish-subscribe protocol
Only data changes are sent on the network
  More efficient network usage than polling
Data is time-stamped by the publisher
Supported in FieldPoint, Lookout, and DataSocket
Built on UDP layer of TCP/IP for better performance
Notes: National Instruments has developed an efficient event driven protocol which only transmits data onto the network if that data has been “subscribed” to by a client application and then only when that data point changes. This means that the Ethernet is only carrying that information which is really useful. Imagine that you want to know, with a 10 millisecond response time, whether a discrete input which changes about once a second is on or off. With a polling scheme, you would need to send 100 requests for the data and get 100 responses every second. With the FieldPoint Ethernet protocol, only one message needs to be sent – when the data changes. This provides the advantages stemming from fewer and smaller Ethernet packets. It also has the advantage that less computing time is spent dealing with redundant information.
The data is time stamped at the publisher, so that even when data delivery is delayed, the time at which the data was acquired is still available.
This is the native protocol used to share Lookout data members and to communicate with Ethernet FieldPoint. National Instruments provides both both an OPC and a DataSocket interface for this protocol so that FieldPoint and Lookout information is available to LabVIEW, Measurement Studio, or any OPC client.
As a technical note, although this protocol works with what is often termed TCP/IP, it uses UDP, not TCP, for more reliable and real-time performance.

## Slide 21: FieldPoint Ethernet (FP-1600)
IP compatibility
  Used with standard networking options
10BaseT, 100BaseTX
  10 or 100 Mbit/s
Event-driven communications
  Efficient use of bandwidth
Notes: The FP-1600 from National Instruments provides direct connection to Ethernet in our FieldPoint family. The FP-1600 is a FieldPoint network interface modules which supports both 10Base-T and 100Base-TX Ethernet, auto-detecting between the two. It uses our event-driven protocol described on the previous slide for efficient networking performance. The support of 100 Mbit/s Ethernet provides for significant additional network efficiency. Since this protocol use IP, it is compatible with existing network options, software, and is familiar to networking professionals.

## Slide 22: Tips on FP-1600 Performance
Don’t oversubscribe to I/O points
Data changes dominate response time
  Especially when many channels change at once
Slower analog input modules keep more resources free
Using more FP-1600s provides greater throughput
Notes: Tips to improve the networking performance of the FP-1600:
Don’t oversubscribe to data items. When the FieldPoint server starts up, it creates a subscription to every data item in the configuration file. You should only have items in the configuration file that you plan to use.
Since the FP-1600 uses an event driven protocol, I/O channels with changing data use up more resources than I/O channels which do not change as often. The worst case delays in getting data occur when many channels change all at once, so consider this when you do your system testing.
The 16 bit analog input modules (including the RTD and Thermocouple modules) have much slower update rates than the 12 bit analog input modules, and so will use up less of the resources of the FP-1600.
Multiple FP-1600 network modules all work in parallel; separating I/O modules among multiple network modules increases throughput.