Jet and Rocket Engine Test System

by

David Hoadley, Ph.D.

Systems Engineering Lead,

Jeff Siegel, Ph.D.

Software Engineering Lead,

Chung-Wen Chen, Ph.D.

Senior Systems Engineer,

V I Engineering, Inc.

Douglas G. Anderson

Director of Operations

Wyle Laboratories – San Bernardino

Ana M. Cool

JRETS/E DAC Technical Lead

Science and Technology Applications, LLC

Category:

Aerospace/Defense

Products Used:

LabVIEW 7.1.1 RT, DSC, FPGA

LabVIEW 8.0 RT

DIAdem 9.1

NI PXI 8196 RT

NI PXI 8187 RT

NI PXI 4472

NI PXI 6653/6651

NI PXI 6250M

NI PXI 6608

NI SCXI 1125

NI SCXI 1520

Enterprise Connectivity Toolsets (Database 1.0.1, Internet 6.0)

Execution Trace Toolkit 1.0

NI Sync 1.2.0

NI DAQmx 8.0

Challenge:

Developing a real-time data acquisition and control system for jet and rocket engine hot fire testing while maintaining the safety of the facility and the test article, reliability and accuracy of data recording, and flexibility and efficiency of configuration are the major system goals.  The channel count, data rates, and event recognition goals presented significant performance challenges.

Solution

Using LabVIEW RT to program a system of five PXI chassis to implement the Data Acquisition and Control (DAC) system. By distributing the system features to separate components, very aggressive performance requirements are reliably achieved. A feature-rich, database-driven host application runs on a server-class PC to provide a user-interface for the system.  The host application provides LabVIEW user-interfaces to configure and run the system, storing relevant settings and results in a relational database. Built-in networking features in LabVIEW allow remote access to calibration and run-time data displays.

Introduction

The Wyle Laboratories San Bernardino Test Facility (Wyle SBO) offers cost effective test solutions to government and industry in the aerospace propulsion market.  The JRETS DAC system is a state-of-the-art, flexible, and high performance system.  Multiple rocket engine test positions have been designed to accommodate engines up to 50,000 lbs of thrust.  Variable fuels such as hydrocarbons and cryogenic propellants can be used, as well as some hybrid solid fuels.  The facility will boast new technologies and methods to mitigate noise and emission controls of combustion products.

System Benefits

A key benefit of the DAC system is the flexibility to generate an event-driven, user-defined test sequence that allows for multiple red-line alarm channels per each event.  Up to 20 simultaneous red-line channels can be defined per event in the automated test sequence, which has a maximum duration of 64 events.  Automatic alarm evaluation with complex alarm clause logic allows for tight multi-level alarms during the high risk activities and more open criteria during the low risk phases of a hot-fire test.  This provides fewer falsely aborted tests and increases the facility throughput.

The DAC system includes a relational database for transducer and test configuration information storage.  It provides advantages such as traceability of test run configurations that increase the value of test data, adding confidence in the measurements and requiring fewer retests to verify behavior.

Figure 1 – JRETS DAC System Overview

System Design

The JRETS DAC system is implemented via six computers, five of which are PXI controllers running LabVIEW RT.  The features of the system are distributed to these resources to provide a modular design and enable reliable, high performance operation.

Data acquisition is accomplished via 8 devices.  Four PXI 4472 boards acquire data from dynamic sensors at 32 KHz.  These reside in the DAQ Achassis, using the PXI 6653 for a timebase clock source via the star trigger lines.  DAQ B includes three PXI 6250M boards programming three SCXI chassis of signal conditioning, with timebase imported from DAQ A via a PXI 6651.  A digital trigger is used to synchronize the start of all analog input tasks.  The eighth input device is a 6511 isolated digital input board, which is used primarily for reading microswitch valve inputs to confirm valve actuation.

Every millisecond, deterministically synchronized acquired data is packaged into a contiguous block or frame and passed to the Master Controller PXI system.  Reflective memory from VMIC is used to transfer data deterministically from controller to controller.  The throughput – 6 MB/second of raw data – and responsiveness required by the entire distributed system, together with LabVIEW RT support for the VMIC 5565 via a LabVIEW RT VISA-based driver, led to our choice of this technology.  The master system reads all input data and evaluates the control sequence and alarms to determine the output state for up to 192 devices.  It has less than a millisecond to accomplish this task in order to be ready once the next frame of data becomes available.  The output values are written to three PXI 6512 boards and added to the data frame in reflective memory immediately after the input data.

The RT Logger system reads all input and output data from reflective memory and then streams data to disk at the predefined rate, up to and including the full sampling rate.  A server component provides engineering unit data to the Host PC via TCP/IP at the greatly reduced rate of 5 Hz.  The server also evaluates calculated channels for the display, such as pressure transducer differences, integrals, or derivatives of signals.

The fifth PXI controller is a watchdog system that monitors the functioning of the Master Controller.  This Slave Controller features parallel digital outputs that follow the master’s values until it detects a failure of the master to update a watchdog signal.  In that event, which has a three millisecond timeout duration, the slave takes control and executes a user-defined safe shutdown sequence.  In the exceedingly unlikely event that both the master and slave software fails, a third level of safety control is invoked; the hardware watchdogs on the 6512 boards will return every valve to its user-specified fail-safe state.  We do not anticipate having to use any of the watchdog features in the system, but they represent a worthwhile ‘insurance policy’ for facility and product safety for such a hard real-time control system.

Figure 2 – JRETS DAC GUI (1 of 4)

A LabVIEW graphical user-interface (GUI) on the Host PC system provides system control for test configuration, sequence specification, transducer calibration, test preparation, test execution and real-time data display, and post-test review.  Three 1600x1200 pixel GUIs that schematically mimic the facility layout for oxidizers (panel 1), fuel systems (panel 3), and the test article environment provide intuitive control capability and status feedback.  A fourth GUI provides additional information: digital indicators and graphs for transducer data and an event log.

Data files are saved in National Instruments TDM format, which provides a great mechanism to attach metadata to the raw values and associate groups of multi-rate data files.  Automatic quick-look reports and ad-hoc data analysis capability are both provided by DIAdem

Conclusion

Based on National Instruments’ LabVIEW RT and PXI platform, we were able to implement a high-performance, flexible, and industry-comparable system within a moderate budget that can be operated and maintained by a minimum set of technicians.  Including hardware, software development, technician training, and other startup costs, alternative solutions were two to three times the cost of our NI-based system.  Tools that extend the LabVIEW development experience, such as the VISTA Statement Coverage Tool, NI Execution Trace Toolkit and Endevo’s GOOP Inheritance Toolkit, enhanced our productivity, increased the quality of our deliverables, and allowed us to plan for effective software maintenance.  The software application is substantial: 207,000 GOBs (a.k.a. lines of code).  LabVIEW RT will remain our first choice for deterministic control system development for the foreseeable future.